## CHP Payback
Company/Customer Name |  | Facility/Site Location
User Inputs:
1. Size CHP Electric Generator (KW) | 1000 | 8. Ave. Electric Usage Rate ($/KWH) |  | 0.12
2. Hours of Cogeneration ( /Year) | 8200 | 9. Electric Demand Charge ($/KW) |  | 10
3. Number of months generating power | 12 | 10. Ave. Natural Gas Rate ($/MMBTU) |  | 7
4. # Years CHP Plant will be Financed | 20 | 11. Gas Rate for CHP ($/MMBTU) |  | 6
5. Interest Rate on Loan for Installed Cost | 5% | 12. Please select Emissions Profile |  | US Average Fossil
6. Investor Pays U.S. Federal Income Tax? | Y | and state/province/region |  | US Average
7. CHP Incentive ($) | 0 | e-GRID Sub-Region Map
Simple Payback (Years) | 3.6618 | 3.4929 | 4.6072 | 5.7114
| Recip. Engine | Micro Turbine | Gas Turbine | Fuel Cell
| 1 | 1 | 1 | 1
CHP Size (KW) | 1000 | 1000 | 1000 | 1000
Installed Cost | 2837000 | 2500000 | 3281000 | 4600000
Federal CHP Investment Tax Credit | 283700 | 250000 | 328100 | 1380000
Cost Less CHP Incentive(s) | 2553300 | 2250000 | 2952900 | 3220000
Ave. Annual Maintenance Cost | 172200 | 98400 | 103320 | 328000
Power Produced (KWH) | 8200000 | 8200000 | 8200000 | 8200000
Annual Electric Saved on Demand | 120000 | 120000 | 120000 | 120000
Annual Electric Savings on Usage | 984000 | 984000 | 984000 | 984000
Annual Gas Cost for Cogeneration | 486559.2417 | 629501.0526 | 701368.0387 | 393600
Recovered Heat (MMBTU/Year) | 36005.3839 | 38294.6474 | 48803.526 | 25912
Annual Gas savings from waste heat use | 252037.6872 | 268062.5316 | 341624.6822 | 181384
Annual O&M cost CHP Plant | 658759.2417 | 727901.0526 | 804688.0387 | 721600
Electric and gas utility savings from CHP | 1356037.6872 | 1372062.5316 | 1445624.6822 | 1285384
Total Savings per year from CHP System | 697278.4455 | 644161.4789 | 640936.6435 | 563784
Average Monthly Savings | 58106.5371 | 53680.1232 | 53411.387 | 46982
Monthly Payment on CHP Plant | 16850.6499 | 14849.0041 | 19487.833 | 21250.5748
Monthly cash flow | 41255.8872 | 38831.1191 | 33923.5539 | 25731.4252
Internal Rate of Return (20 Year cash flow) | 27.08% | 28.44% | 21.24% | 16.71%
CO2 savings per year (Tons) | 4632.5021 | 3399.44 | 3467.5734 | 4801.7067
Equivalent # of vehicles | 888.4944 | 651.9983 | 665.066 | 920.9471
Equivalent # of homes | 620.5816 | 455.3975 | 464.5248 | 643.2486
Assumptions
Typical Size Range | 65KW-15MW | 30KW-2000KW | 1MW - 50MW | 200 - 2000 KW
Average Installed cost ($/KW) | 2837 | 2500 | 3281 | 4600
Total Average CHP System Efficiency | 78.9% | 63.1% | 65.7% | 82%
Avg. Heat Recovery from Prime Mover | 44.4% | 36.5% | 41.75% | 39.5%
Gas Input (MMBTU/Hr) | 9.8894 | 12.7947 | 14.2554 | 8
O&M Cost ($/KWH) | 0.021 | 0.012 | 0.0126 | 0.04
Notes | Less than a 50 KW Engine is considered Micro-CHP | Package multiple Micro turbines to reach 2 MW | Size starts at 1000KW | MCFC & PAFC
Disclaimer: This calculator was prepared for work sponsored by the Energy Solutions Center Inc. Neither The Energy Solutions Center, any member of The Energy Solutions Center, nor any person on behalf of any or all of them: a. Makes any warranty or representation, express or implied, with respect to the accuracy, completeness, or usefulness of the information contained in this calculation or report, or b. Assumes any liability with respect to the use of or for damages resulting from the use of any information disclosed in this application or report. Notes: CO2 savings are based off the marginal power mix for U.S. States as well as a few provinces. Displaced gas heat = recovered heat / 80% boiler efficiency. You may enter the "all-in" average cost per KWH and 0 for the Demand charge or for a more accurate calculation enter the average cost per KWH and the demand cost per KW. Rules and qualifications for the Federal CHP Tax Credit can be found at: https://www.epa.gov/chp/dchpp-chp-policies-and-incentives-database . Life Cycle Cost analysis uses 1% Fuel and 1% Maintenance inflation rates per year.

## Overview (hidden)
Combined Heat & Power (CHP) Simple Payback Analysis
This tool provides a simple payback calculation for various CHP technologies based off the size and energy rates. The calculations use average pricing, efficiencies, & maintenance costs provided in the CHP Technology Catalogs available from the Combined Heat and Power partnership of the EPA.
The results produced by use of this tool are intended solely as a preliminary evaluation of a potential CHP installation. For a more detailed and exact evaluation you should seek the assistance of a qualified engineering firm with input from the appropriate manufacturers of power generation equipment.

## Assumptions (hidden)
Assumptions
LHV Natural Gas BTU/SCF |  |  | 905 | HHV Natural Gas BTU/SCF |  |  | 1030
Electric Utility CO2 emmisions (#/KWH) |  |  | #N/A |  |  | Natural Gas CO2 (#/MMBTU) | 119.741
State Historical Tables for 2010 - Sort by Energy Source Released: December 2011 Next Update: November 2012
Costs from EPA Catalog of CHP Technologies | [9 empty] | 2008 Handbook data
Gas Turbine Performance Parameters (March 2015 Catalog) | [9 empty] | Gas Turbine Performance Parameters 2008
Electricity Capacity (kW) |  |  | 3304 | 7038 | 9950 | 20336 | 44488 | Tab 3.2 |  | Electricity Capacity (kW) |  |  | 1150 | 5457 | 10239 | 25000 | 40000
Installed Cost (2013 $/kW) |  |  | 3281 | 2080 | 1976 | 1518 | 1248 | Tab 3.2 |  | Basic Tot Installed Cost ($/kW) |  |  | 3324 | 1314 | 1298 | 1097 | 972
Electrical Efficiency (%), HHV |  |  | 23.95% | 28.9% | 27.34% | 33.24% | 35.96% | Tab 3.2 |  | Electrical Efficiency (%), HHV |  |  | 21.27% | 27.72% | 28.44% | 34.3% | 37%
Avg. Heat Recovery |  |  | 41.75% | 41.5% | 42.16% | 37.26% | 32.84% |  |  | Avg. Heat Recovery |  |  | 45.03% | 42.08% | 39.96% | 36.4% | 35.1%
MMBTU/Hr/KW |  |  | 0.014255 | 0.011807 | 0.012482 | 0.010263 | 0.009488 |  |  | MMBTU/Hr/KW |  |  | 0.016087 | 0.012314 | 0.012003 | 0.009944 | 0.00922
Total O&M Costs, $/kWh |  |  | 0.0126 | 0.0123 | 0.012 | 0.0093 | 0.0092 | Tab 3.6 |  | Total O&M Costs, $/kWh |  |  | 0.0111 | 0.0074 | 0.007 | 0.0049 | 0.0042
Fuel Input (MMBtu/hr) |  |  | 47.1 | 83.1 | 124.2 | 208.7 | 422.1 | Tab 3.2 |  | Fuel Input (MMBtu/hr) |  |  | 18.5 | 67.2 | 122.9 | 248.6 | 368.8
Total CHP Efficiency (%), HHV |  |  | 65.7% | 70.4% | 69.5% | 70.5% | 68.8% | Tab 3.2 |  | Total CHP Efficiency (%), HHV |  |  | 66.3% | 69.8% | 68.4% | 70.7% | 72.1%
Note that 5457 KW CT column is used for 3500 KW to 10,238 KW.
Micro Turbines (March 2015 Catalog) | [9 empty] | Micro Turbines 2008
Net Electricity Capacity (kW) |  |  | 28 | 61 | 190 | 240 | 320 | 950 | Tab. 5-2 | Nominal Electricity Capacity (kW) |  |  | 30 | 65 | 250
Total Installed Cost ($/kW) |  |  | 4300 | 3220 | 3150 | 2720 | 2580 | 2500 | Tab. 5-2 | Total Installed Cost ($/kW) |  |  | 2970 | 2490 | 2440
Electrical Efficiency (%), HHV |  |  | 21.9% | 23.7% | 26.6% | 26% | 28% | 26.6% | Tab. 5-2 | Electrical Efficiency (%), HHV |  |  | 22.6% | 24.6% | 26.09%
Avg. Heat Recovery |  |  | 48.1% | 46.7% | 36.4% | 40.9% | 39.5% | 36.5% |  | Avg. Heat Recovery |  |  | 41.2% | 46.6% | 37.91%
MMBTU/Hr/KW |  |  | 0.0155 | 0.014361 | 0.012795 | 0.013079 | 0.012169 | 0.012795 |  | MMBTU/Hr/KW |  |  | 0.014067 | 0.013462 | 0.01266
Total O&M Costs, $/kWh |  |  | 0.016 | 0.013 | 0.016 | 0.011 | 0.009 | 0.012 | Tab. 5-5 | Total O&M Costs, $/kWh |  |  | 0.02 | 0.0175 | 0.016
O&M Cost range from catalog |  | Not using ranges in 2015 | [7 empty] | O&M Cost range from catalog |  |  | .015-.025 | .013-.022 | .012-.02
Fuel Input (MMBtu/hr) |  |  | 0.434 | 0.876 | 2.431 | 3.139 | 3.894 | 12.155 | Tab. 5-2 | Fuel Input (MMBtu/hr) |  |  | 0.422 | 0.875 | 3.165
Total CHP Efficiency (%), HHV |  |  | 70% | 70.4% | 63% | 66.9% | 67.5% | 63.1% | Tab. 5-2 | Total CHP Efficiency (%), HHV |  |  | 63.8% | 71.2% | 64%
No O&M for 30KW model so use highest O&M used in analysis | [9 empty] | Electrical efficiencies are net of parasitic and conversion losses. Fuel gas compressor needs based on 1 psi inlet supply.
Gas Engine (March 2015 Catalog) | [9 empty] | Gas Engine 2008
Baseload Electric Capacity (kW) * |  |  | 100 | 633 | 1121 | 3326 | 9341 | Tab. 2-2 |  | Baseload Electric Capacity (kW) * |  |  | 100 | 500 | 1000 | 3000 | 5000
Total Installed Cost ($/kW) * |  |  | 2900 | 2837 | 2366 | 1801 | 1433 | Tab. 2-2 |  | Total Installed Cost ($/kW) * |  |  | 3000 | 2600 | 2000 | 1450 | 1250
Electrical Efficiency (%), HHV |  |  | 27% | 34.5% | 36.8% | 40.4% | 41.6% | Tab. 2-2 |  | Electrical Efficiency (%), HHV |  |  | 28.4% | 34.6% | 35% | 36% | 39%
Avg. Heat Recovery |  |  | 53% | 44.4% | 41.6% | 37.9% | 34.9% |  |  | Avg. Heat Recovery |  |  | 50.6% | 43.4% | 44% | 37% | 35%
MMBTU/Hr/KW |  |  | 0.0126 | 0.0098894 | 0.0092596 | 0.0084546 | 0.0082068 |  |  | MMBTU/Hr/KW |  |  | 0.012 | 0.00986 | 0.00976 | 0.0094933 | 0.008758
Total O&M Costs, $/kWh |  |  | 0.024 | 0.021 | 0.019 | 0.016 | 0.0085 | Tab 2-6 |  | Total O&M Costs, $/kWh |  |  | 0.022 | 0.016 | 0.013 | 0.01 | 0.009
Fuel Input (MMBtu/hr) |  |  | 1.26 | 6.26 | 10.38 | 28.12 | 76.66 | Tab. 2-2 |  | Fuel Input (MMBtu/hr) |  |  | 1.2 | 4.93 | 9.76 | 28.48 | 43.79
Total Efficiency (%) |  |  | 80% | 78.9% | 78.4% | 78.3% | 76.5% | Tab. 2-2 |  | Total Efficiency (%) |  |  | 79% | 78% | 79% | 73% | 74%
100KW O&M was a range that was averaged | [9 empty] | Effective Electrical Efficiency = (CHP electric power output)/(Total fuel into CHP system – total heat recovered/0.8); Equivalent to 3412 Btu/kWh/Net Heat Rate
Total CHP Efficiency = (net electric generated + net thermal energy recovered)/total engine fuel input
Fuel Cells (March 2015 Catalog) | [9 empty] | Fuel Cells
Fuel Cell Type |  |  | PEMFC | SOFC | MCFC | PAFC | MCFC |  |  | Fuel Cell Type |  |  | PEM | PAFC
Nominal Electricity Capacity (kW) |  |  | 0.7 | 1.5 | 300 | 400 | 1400 | Tab. 6-3 |  | Nominal Electricity Capacity (kW) |  |  | 10 | 200
Total package Cost ($/kW) |  |  | 22000 | 23000 | 10000 | 7000 | 4600 | Tab. 6-4 |  | Total Installed Cost ($/kW) |  |  | 9100 | 6310
Electrical Efficiency (% HHV) |  |  | 35.3% | 54.4% | 47% | 34.3% | 42.5% | Tab. 6-3 |  | Electrical Efficiency (% HHV) |  |  | 30% | 33%
Avg. Heat Recovery |  |  | 50.7% | 19.6% | 35% | 46.7% | 39.5% |  |  | Avg. Heat Recovery |  |  | 35% | 48%
MMBTU/Hr/KW |  |  | 0.0097143 | 0.0062667 | 0.0073333 | 0.01 | 0.008 |  |  | MMBTU/Hr/KW |  |  | 0.01 | 0.0095
O&M Costs ($/kW) |  |  | 0.06 | 0.055 | 0.045 | 0.036 | 0.04 | Tab. 6-4 |  | O&M Costs ($/kW) |  |  | 0.033 | 0.038
Fuel Input (MMBtu/hr) |  |  | 0.0068 | 0.0094 | 2.2 | 4 | 11.2 | Tab. 6-3 |  | Fuel Input (MMBtu/hr) |  |  | 0.1 | 1.9
Total CHP Efficiency (%), HHV |  |  | 86% | 74% | 82% | 81% | 82% | Tab. 6-3 |  | Total CHP Efficiency (%), HHV |  |  | 65% | 81%
Electrical efficiencies are net of parasitic and conversion losses.
Source of data above : U.S. EPA, Technolgy Catalogs March 2015 | [9 empty] | Notes 2008 to 2015 Guide Data
http://www.epa.gov/chp/chp-technologies | [9 empty] | CT Installed costs rose about 25%, Electrical and heat efficicincies fluctuated +/1 1% across board, and O&M rose slightly
http://www.epa.gov/chp/catalog-chp-technologies | [9 empty] | Microturbines added 3 more model sizes. Net electrical capacity takes into account parasitic loads for the compressor.
Engine prices went up for larger engines, didn’t change much for smaller engines
A few new sizes and types of fuel cels were added to the mix. The cost of 1 1400 KW system is 25% less per KW than previos systems.
Overall: Some paybacks increased while others decreased. And the range of sizes included in the tool is broader than in the previous tool.
Assumptions to show on website:
[10 empty] | Assumptions | Reciprocating Engine | Micro Turbine | Gas Turbine | Fuel Cell
[10 empty] | Typical Size Range | 65KW-15MW | 30KW-2000KW | 1MW - 50MW | 200 - 2000 KW
[10 empty] | Average Installed cost ($/KW) | $1,433 - $2,900 | $2,500 - $4,300 | $1,250 - $3,300 | $4,600 - $10,000
[10 empty] | Total Average CHP System Efficiency | 78.42% | 66.82% | 68.98% | 81.67%
[10 empty] | O&M Cost ($/KWH) | 0.0177 | 0.012833 | 0.01108 | 0.040333
[10 empty] | Notes | Less than a 65KW Engine is considered Micro-CHP | Can package multiple Micro turbines to reach 2 MW | Size starts at 1000KW | MCFC & PAFC
Tax Cedits: | www.epa.gov/chp/policies/database.html
Business Energy Investment Tax Credit (ITC)
CHP | 10%
Micro Turbine | 10% | Cap at $200/KW
Fuel Cell | 30% | Cap at $1500 per >5KW
Maxium years payback for Out of Range assumption |  |  |  | 20
10 year cash flow
Year | Reciprocating Engine | Micro Turbine | Gas Turbine | Fuel Cell
0 | -2553300 | -2250000 | -2952900 | -3220000
1 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
2 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
3 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
4 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
5 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
6 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
7 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
8 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
9 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
10 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
11 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
12 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
13 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
14 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
15 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
16 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
17 | 697278.4455 | 644161.4789 | 640936.6435 | 563784
18 | 697278.4455 | 644161.4789 | 640936.6435 | 563784 |  |  | Regions
19 | 697278.4455 | 644161.4789 | 640936.6435 | 563784 |  | Drop down list | eGRID US Average All Sources 2016 | eGRID_US_Average_All_Sources_2016 | eGRID_US_Average_Fossil_2016 | eGrid_Subregions_Average_All_Sources_2016 | eGrid_Subregions_Average_Fossil_2016 | NERC_Average_All_Sources_2016 | NERC_Average_Fossil_2016 | Canadian_Average_All_Sources_2011
20 | 697278.4455 | 644161.4789 | 640936.6435 | 563784 |  | US Average | eGRID US Average Fossil 2016 | US Average | US Average | ASCC Alaska Grid | ASCC Alaska Grid | Alaska Systems Coordinating Council | Alaska Systems Coordinating Council | Canada Average
[6 empty] | Alabama | eGrid Subregions Average All Sources 2016 | Alaska | Alaska | ASCC Miscellaneous | ASCC Miscellaneous | Florida Reliability Coordinating Council | Florida Reliability Coordinating Council | Alberta
[6 empty] | Alaska | eGrid Subregions Average Fossil 2016 | Alabama | Alabama | ERCOT All | ERCOT All | Hawaiian Islands Coordinating Council | Hawaiian Islands Coordinating Council | British Columbia
[6 empty] | Arizona | NERC Average All Sources 2016 | Arkansas | Arkansas | FRCC All | FRCC All | Midwest Reliability Organization | Midwest Reliability Organization | Manitoba
[6 empty] | Arkansas | NERC Average Fossil 2016 | Arizona | Arizona | HICC Miscellaneous | HICC Miscellaneous | No NERC region | No NERC region | New Brunswick
[6 empty] | California | Canadian Average All Sources 2011 | California | California | HICC Oahu | HICC Oahu | Northeast Power Coordinating Council | Northeast Power Coordinating Council | Newfoundland
[6 empty] | Colorado |  | Colorado | Colorado | MRO East | MRO East | Reliability First Corporation | Reliability First Corporation | Nova Scotia
[6 empty] | Connecticut |  | Connecticut | Connecticut | MRO West | MRO West | SERC Reliability Corporation | SERC Reliability Corporation | Ontario
[6 empty] | District of Columbia |  | District of Columbia | District of Columbia | NPCC Long Island | NPCC Long Island | Southwest Power Pool | Southwest Power Pool | Prince Edward Island
[6 empty] | Delaware |  | Delaware | Delaware | NPCC New England | NPCC New England | Texas Regional Entity | Texas Regional Entity | Quebec
[6 empty] | Florida |  | Florida | Florida | NPCC NYC/Westchester | NPCC NYC/Westchester | Western Electricity Coordinating Council | Western Electricity Coordinating Council | Saskatchewan
[6 empty] | Georgia |  | Georgia | Georgia | NPCC Upstate NY | NPCC Upstate NY
[6 empty] | Hawaii |  | Hawaii | Hawaii | RFC East | RFC East
[6 empty] | Idaho |  | Iowa | Iowa | RFC Michigan | RFC Michigan
[6 empty] | Illinois |  | Idaho | Idaho | RFC West | RFC West
[6 empty] | Indiana |  | Illinois | Illinois | SERC Midwest | SERC Midwest
[6 empty] | Iowa |  | Indiana | Indiana | SERC Mississippi Valley | SERC Mississippi Valley
[6 empty] | Kansas |  | Kansas | Kansas | SERC South | SERC South
[6 empty] | Kentucky |  | Kentucky | Kentucky | SERC Tennessee Valley | SERC Tennessee Valley
[6 empty] | Louisiana |  | Louisiana | Louisiana | SERC Virginia/Carolina | SERC Virginia/Carolina
[6 empty] | Maine |  | Massachusetts | Massachusetts | SPP North | SPP North
[6 empty] | Maryland |  | Maryland | Maryland | SPP South | SPP South
[6 empty] | Massachusetts |  | Maine | Maine | WECC California | WECC California
[6 empty] | Michigan |  | Michigan | Michigan | WECC Northwest | WECC Northwest
[6 empty] | Minnesota |  | Minnesota | Minnesota | WECC Rockies | WECC Rockies
[6 empty] | Mississippi |  | Missouri | Missouri | WECC Southwest | WECC Southwest
[6 empty] | Missouri |  | Mississippi | Mississippi
[6 empty] | Montana |  | Montana | Montana
[6 empty] | Nebraska |  | North Carolina | North Carolina
[6 empty] | Nevada |  | North Dakota | North Dakota
[6 empty] | New Hampshire |  | Nebraska | Nebraska
[6 empty] | New Jersey |  | New Hampshire | New Hampshire
[6 empty] | New Mexico |  | New Jersey | New Jersey
[6 empty] | New York |  | New Mexico | New Mexico
[6 empty] | North Carolina |  | Nevada | Nevada
[6 empty] | North Dakota |  | New York | New York
[6 empty] | Ohio |  | Ohio | Ohio
[6 empty] | Oklahoma |  | Oklahoma | Oklahoma
[6 empty] | Oregon |  | Oregon | Oregon
[6 empty] | Pennsylvania |  | Pennsylvania | Pennsylvania
[6 empty] | Rhode Island |  | Rhode Island | Rhode Island
[6 empty] | South Carolina |  | South Carolina | South Carolina
[6 empty] | South Dakota |  | South Dakota | South Dakota
[6 empty] | Tennessee |  | Tennessee | Tennessee
[6 empty] | Texas |  | Texas | Texas
[6 empty] | Utah |  | Utah | Utah
[6 empty] | Vermont |  | Virginia | Virginia
[6 empty] | Virginia |  | Vermont | Vermont
[6 empty] | Washington |  | Washington | Washington
[6 empty] | West Virginia |  | Wisconsin | Wisconsin
[6 empty] | Wisconsin |  | West Virginia | West Virginia
[6 empty] | Wyoming |  | Wyoming | Wyoming
Canada
Alberta
Ontario
New Brunswick
Nova Scotia
Removed from List since no marginal mix avaialble
Canada Average
Alberta
British Columbia
Manitoba
Newfoundland
Prince Edward Island
Quebec
Saskatchewan

## Life Cycle Cost (hidden)
Life Cycle Cost Analysis - CHP
| Assumptions: | Fuel Inflation Rate |  | 1% | /yr | Maint. Inflation rate |  | 1% | /yr
Assume no loan on installed cost. All capital and installation costs paid in year 0.
| Grid Power |  |  | Reciprocating Engine |  |  | Micro Turbine |  |  | Gas Turbine |  |  | Fuel Cell
Year | Installed cost | Energy Cost | Maint. Cost | Installed cost | Energy Cost | Maint. Cost | Installed cost | Energy Cost | Maint. Cost | Installed cost | Energy Cost | Maint. Cost | Installed cost | Energy Cost | Maint. Cost
0 | 0 |  |  | 2553300 |  |  | 2250000 |  |  | 2952900 |  |  | 3220000
1 | 0 | 994000 | 0 | 0 | 234521.5545 | 172200 | 0 | 361438.5211 | 98400 | 0 | 359743.3565 | 103320 | 0 | 212216 | 328000
2 | 0 | 1003940 | 0 | 0 | 236866.77 | 173922 | 0 | 365052.9063 | 99384 | 0 | 363340.7901 | 104353.2 | 0 | 214338.16 | 331280
3 | 0 | 1013979.4 | 0 | 0 | 239235.4377 | 175661.22 | 0 | 368703.4353 | 100377.84 | 0 | 366974.198 | 105396.732 | 0 | 216481.5416 | 334592.8
4 | 0 | 1024119.194 | 0 | 0 | 241627.7921 | 177417.8322 | 0 | 372390.4697 | 101381.6184 | 0 | 370643.94 | 106450.6993 | 0 | 218646.357 | 337938.728
5 | 0 | 1034360.3859 | 0 | 0 | 244044.07 | 179192.0105 | 0 | 376114.3744 | 102395.4346 | 0 | 374350.3794 | 107515.2063 | 0 | 220832.8206 | 341318.1153
6 | 0 | 1044703.9898 | 0 | 0 | 246484.5107 | 180983.9306 | 0 | 379875.5181 | 103419.3889 | 0 | 378093.8832 | 108590.3584 | 0 | 223041.1488 | 344731.2964
7 | 0 | 1055151.0297 | 0 | 0 | 248949.3559 | 182793.7699 | 0 | 383674.2733 | 104453.5828 | 0 | 381874.822 | 109676.262 | 0 | 225271.5603 | 348178.6094
8 | 0 | 1065702.54 | 0 | 0 | 251438.8494 | 184621.7076 | 0 | 387511.016 | 105498.1186 | 0 | 385693.5702 | 110773.0246 | 0 | 227524.2759 | 351660.3955
9 | 0 | 1076359.5654 | 0 | 0 | 253953.2379 | 186467.9247 | 0 | 391386.1262 | 106553.0998 | 0 | 389550.5059 | 111880.7548 | 0 | 229799.5186 | 355176.9994
10 | 0 | 1087123.161 | 0 | 0 | 256492.7703 | 188332.604 | 0 | 395299.9875 | 107618.6308 | 0 | 393446.011 | 112999.5624 | 0 | 232097.5138 | 358728.7694
11 | 0 | 1097994.3927 | 0 | 0 | 259057.698 | 190215.93 | 0 | 399252.9873 | 108694.8171 | 0 | 397380.4711 | 114129.558 | 0 | 234418.489 | 362316.0571
12 | 0 | 1108974.3366 | 0 | 0 | 261648.275 | 192118.0893 | 0 | 403245.5172 | 109781.7653 | 0 | 401354.2758 | 115270.8536 | 0 | 236762.6739 | 365939.2177
13 | 0 | 1120064.08 | 0 | 0 | 264264.7577 | 194039.2702 | 0 | 407277.9724 | 110879.583 | 0 | 405367.8186 | 116423.5621 | 0 | 239130.3006 | 369598.6099
14 | 0 | 1131264.7208 | 0 | 0 | 266907.4053 | 195979.6629 | 0 | 411350.7521 | 111988.3788 | 0 | 409421.4968 | 117587.7977 | 0 | 241521.6036 | 373294.596
15 | 0 | 1142577.368 | 0 | 0 | 269576.4793 | 197939.4595 | 0 | 415464.2596 | 113108.2626 | 0 | 413515.7117 | 118763.6757 | 0 | 243936.8196 | 377027.5419
16 | 0 | 1154003.1416 | 0 | 0 | 272272.2441 | 199918.8541 | 0 | 419618.9022 | 114239.3452 | 0 | 417650.8688 | 119951.3125 | 0 | 246376.1878 | 380797.8174
17 | 0 | 1165543.1731 | 0 | 0 | 274994.9666 | 201918.0427 | 0 | 423815.0912 | 115381.7387 | 0 | 421827.3775 | 121150.8256 | 0 | 248839.9497 | 384605.7955
18 | 0 | 1177198.6048 | 0 | 0 | 277744.9162 | 203937.2231 | 0 | 428053.2422 | 116535.556 | 0 | 426045.6513 | 122362.3338 | 0 | 251328.3492 | 388451.8535
19 | 0 | 1188970.5908 | 0 | 0 | 280522.3654 | 205976.5953 | 0 | 432333.7746 | 117700.9116 | 0 | 430306.1078 | 123585.9572 | 0 | 253841.6327 | 392336.372
20 | 0 | 1200860.2967 | 0 | 0 | 283327.5891 | 208036.3613 | 0 | 436657.1123 | 118877.9207 | 0 | 434609.1689 | 124821.8168 | 0 | 256380.049 | 396259.7357
| 0 | 21886889.9708 | 0 | 2553300 | 5163931.0455 | 3791672.4879 | 2250000 | 7958516.2389 | 2166669.9931 | 2952900 | 7921190.4047 | 2275003.4927 | 3220000 | 4672784.9518 | 7222233.3103
|  | Life Cycle Cost = | 21886889.9708 |  | Life Cycle Cost = | 11508903.5334 |  | Life Cycle Cost = | 12375186.232 |  | Life Cycle Cost = | 13149093.8974 |  | Life Cycle Cost = | 15115018.2621
|  |  |  | Capital Cost | Maintenance Cost | Energy Cost
|  |  | Grid Power | 0 | 0 | 21886889.9708
|  |  | Reciprocating Engine | 2553300 | 3791672.4879 | 5163931.0455
|  |  | Micro Turbine | 2250000 | 2166669.9931 | 7958516.2389
|  |  | Gas Turbine | 2952900 | 2275003.4927 | 7921190.4047
|  |  | Fuel Cell | 3220000 | 7222233.3103 | 4672784.9518

## Carbon Calc 041118 (hidden)
Commercial Carbon Calculator
Developed by:
[10 empty] | eGrid Data (2018 Update, 2016 Data) | [31 empty] | Canada Data | [18 empty] | Emissions Summary |  |  |  |  | Other Data | [5 empty] | Lists
[42 empty] | CO2 Emissions | [5 empty] | SOX and NOX Emissions | [7 empty] | Canadian Average All Sources 2011 |  |  |  |  | eGRID US (2016), NIR and NPRI Canada (2011) |  |  |  |  | NOX Emission Factors, EPA AP-42 Section 1.4 Natural Gas Combustion, Table 3.4-1 |  |  |  | Unit Conversions |  | Consumption | Regions |  | Emissions Profile
[10 empty] | eGRID2018 year 2016 file state sequence number | State abbreviation | State nameplate capacity (MW) | State annual heat input (MMBtu) | State annual net generation (MWh) | State annual NOx emissions (tons) | State annual SO2 emissions (tons) | State annual CO2 emissions (tons) | State annual NOx total output emission rate (lb/MWh) | State annual SO2 total output emission rate (lb/MWh) | State annual CO2 total output emission rate (lb/MWh) | State annual NOx input emission rate (lb/MMBtu) | State ozone season NOx input emission rate (lb/MMBtu) | State annual SO2 input emission rate (lb/MMBtu) | State annual CO2 input emission rate (lb/MMBtu) | State annual NOx fossil fuel output emission rate (lb/MWh) | State annual SO2 fossil fuel output emission rate (lb/MWh) | State annual CO2 fossil fuel output emission rate (lb/MWh) | State annual NOx fossil fuel input emission rate (lb/MMBtu) | State annual SO2 fossil fuel input emission rate (lb/MMBtu) | State annual CO2 fossil fuel input emission rate (lb/MMBtu) | State annual coal net generation (MWh) | State annual oil net generation (MWh) | State annual gas net generation (MWh) | State annual other fossil net generation (MWh) | State coal generation percent (resource mix) | State oil generation percent (resource mix) | State gas generation percent (resource mix) | State other fossil generation percent (resource mix) | State total combustion generation percent (resource mix) | Total Annual Heat Rate (Btu/kWh) | Fossil Annual Heat Rate (Btu/kWh) |  | CO2 - g CO2 eq/kWh |  | CO2 - lb CO2 eq/MWh |  |  |  | SOX (t)1 | NOX (t)1 | SOX (pounds) | NOX (pounds) | Generation (GWh)2 | SO2 output emission rate (lb/MWh) | NOX output emission rate (lb/MWh) | Canada Province | 2011 CO2 Emission Rate (lb/MWh)1 | 2011 NOX Emission Rate (lb/MWh)2 | 2011 SO2 Emission Rate (lb/MWh)2,3 | 2004 Province Annual Heat Rate (Btu/kWh) | State | CO2 Emission Rate (lb/MWh) | SO2 Emission Rate (lb/MWh) | NOX Emission Rate (lb/MWh) | Annual Heat Rate (Btu/kWh) | Pollutant | # of Tests | Emission Factor (lb/106 scf) | Relative St. Dev (%) | Value | Units | Monthly | US Average | US Average | US Average Fossil | US_Average_All_Sources | US_Average_Fossil | eGrid_Subregions_Ave_All_Sources | eGrid_Subregions_Average_Fossil | NERC_Average_All_Sources | NERC_Average_Fossil | Canadian_Average_All_Sources
User Input | [9 empty] | N/A | US Average | 1515006.8 | 24681443314.815 | 4075322641.089 | 1469046.579 | 1626230.118 | 2034489329.815 | 1.0157 | 0.85008 | 990.4938 | 0.14996 | 0.14522 | 0.12141 | 154.6354 | 1.4468 | 1.2484 | 1565.2376 | 0.14053 | 0.1241 | 164.0769 | 1239148653.12 | 24194840.375 | 1377456321.683 | 13889068.879 | 30.0681 | 1.9782 | 30.3639 | 0.30406 | 66.9016 | 6056.3164 | 8715.3973 |  | Generation Intensity | Consumption Intensity | Generation Intensity | Consumption Intensity | Losses1 | Canada Average | 294098.9672 | 184706.7366 | 648376465.0794 | 407208165.6166 | 568000 | 1.1415 | 0.71692 | Canada Average | 361.5584 | 0.71692 | 1.1415 | 3634 | US Average | 990.4938 | 0.85008 | 1.0157 | 6056.3164 | NOx (Small-Unc.) | 18 | 104 | 51% | 1.1023 | short ton/metric ton | Annual | Alaska | AK | eGrid Subregions Average Fossil | US Average | US Average | ASCC Alaska Grid | ASCC Alaska Grid | Alaska Systems Coordinating Council | Alaska Systems Coordinating Council | Canada Average
|  |  | Comparison Cases | [6 empty] | 1 | AK | 3439.3 | 42553080.628 | 6335033.511 | 21008.135 | 1748.465 | 2932682.544 | 6.632 | 0.552 | 925.862 | 0.987 | 0.963 | 0.082 | 137.836 | 9.265 | 0.778 | 1311.311 | 0.983 | 0.083 | 139.146 | 594138.933 | 831329.647 | 3040487.303 | 0 | 9.3751 | 13.1178 | 47.9767 | 0 | 71.1106 | 6717.1043 | 9442.4321 | Canada Average | 164 | 180 | 361.5584 | 396.8324 | 9.756% | Alberta | 114491.811 | 84030.1175 | 252410936.2786 | 185254477.6454 | 64600 | 3.9073 | 2.8677 | Alberta | 1629.2174 | 2.8677 | 3.9073 | 10177 | AK | 925.862 | 0.552 | 6.632 | 6717.1043 | NOx (Small-Low NOx) | 5 | 50 | 54% | 0.099976 | mmbtu/therm |  | Alabama | AL | Canadian Average All Sources | Alaska | Alaska | ASCC Miscellaneous | ASCC Miscellaneous | Florida Reliability Coordinating Council | Florida Reliability Coordinating Council | Alberta
Description | Reference Case |  | Recip | Micro Turbine |  | Gas Turbine | Fuel Cell | #5 | #6 | 2 | AL | 38353.5 | 824393497.065 | 142863240.209 | 29880.561 | 28836.22 | 65211148.281 | 0.418 | 0.404 | 912.917 | 0.072 | 0.064 | 0.07 | 158.204 | 0.604 | 0.557 | 1404.737 | 0.069 | 0.064 | 161.441 | 34258405.453 | 45832.367 | 57803618.427 | 24053.044 | 23.9799 | 0.032081 | 40.4608 | 0.016836 | 66.8242 | 5770.5082 | 8635.3626 | Alberta | 739 | 1000 | 1629.2174 | 2204.6244 | 35.32% | British Columbia | 138.7048 | 2088.8574 | 305791.3652 | 4605136.7282 | 56300 | 0.0054315 | 0.081796 | British Columbia | 24.9123 | 0.081796 | 0.0054315 | 437 | AL | 912.917 | 0.404 | 0.418 | 5770.5082 | NOx (Small-Low NOx/FGR) | 15 | 32 | 18% | 2000 | pounds/short ton |  | Arkansas | AR |  | Alabama | Alabama | ERCOT All | ERCOT All | Hawaiian Islands Coordinating Council | Hawaiian Islands Coordinating Council | British Columbia
|  | Gas Consumption (MMBTU/Yr) | 81093.207 | 104916.8421 |  | 116894.6731 | 65600 |  |  | 3 | AR | 19535.8 | 387648456.454 | 60445059.072 | 27939.914 | 48693.672 | 33717770.257 | 0.924 | 1.611 | 1115.65 | 0.144 | 0.146 | 0.251 | 173.961 | 1.29 | 2.235 | 1611.949 | 0.142 | 0.247 | 177.91 | 23800070.486 | 42363.246 | 18171187.005 | 5636.773 | 39.3747 | 0.070086 | 30.0623 | 0.0093254 | 71.7827 | 6413.2365 | 8934.2389 | British Columbia | 11.3 | 12 | 24.9123 | 26.4555 | 6.195% | Manitoba | 664.7416 | 442.0757 | 1465502.6089 | 974608.8956 | 35100 | 0.041752 | 0.027767 | Manitoba | 7.3194 | 0.027767 | 0.041752 | 300 | AR | 1115.65 | 1.611 | 0.924 | 6413.2365 | NOx (Large Wall-Fired-Low NOx) | 5 | 136 | 37% | 453.592 | grams/pound |  | Arizona | AZ |  | Arkansas | Arkansas | FRCC All | FRCC All | Midwest Reliability Organization | Midwest Reliability Organization | Manitoba
Electricity Consumption (kWh/yr) | 8200000 | [8 empty] | 4 | AZ | 40134.7 | 602858093.581 | 108734630.779 | 33982.223 | 12955.197 | 50682559.953 | 0.625 | 0.238 | 932.225 | 0.113 | 0.103 | 0.043 | 168.141 | 1.034 | 0.399 | 1567.773 | 0.112 | 0.043 | 169.228 | 30403391.9 | 51594.649 | 34182807.969 | 0 | 27.9609 | 0.04745 | 31.4367 | 0 | 59.6423 | 5544.3063 | 9295.8813 | Manitoba | 3.32 | 3.5 | 7.3194 | 7.7162 | 5.422% | New Brunswick | 4865.9542 | 7004.9459 | 10727579.8765 | 15443243.7219 | 11200 | 0.95782 | 1.3789 | New Brunswick | 976.6486 | 1.3789 | 0.95782 | 2720 | AZ | 932.225 | 0.238 | 0.625 | 5544.3063 | NOx (Large Wall-Fired-FGR) | 4 | 101 | 25% |  |  |  | California | CA |  | Arizona | Arizona | HICC Miscellaneous | HICC Miscellaneous | No NERC region | No NERC region | New Brunswick
|  | Displaced gas heat (MMBTU/Yr): = recovered heat /80% boiler efficiency | 45006.7299 | 47868.3092 |  | 61004.4075 | 32390 |  |  | 5 | CA | 106792.9 | 807555205.269 | 197323836.964 | 46856.782 | 3611.393 | 44648567.221 | 0.475 | 0.037 | 452.541 | 0.116 | 0.113 | 0.009 | 110.577 | 0.648 | 0.01 | 867.421 | 0.088 | 0.001 | 117.897 | 318875.815 | 174814.33 | 97006836.053 | 1426815.666 | 0.1616 | 0.088593 | 49.1612 | 0.72308 | 53.4817 | 4092.5375 | 7652.2146 | New Brunswick | 443 | 450 | 976.6486 | 992.081 | 1.58% | Newfoundland | 3063.064 | 3269.4463 | 6752892.1557 | 7207886.603 | 41300 | 0.16351 | 0.17453 | Newfoundland | 44.9743 | 0.17453 | 0.16351 | 365 | CA | 452.541 | 0.037 | 0.475 | 4092.5375 | NOx (Large Wall-Fired Unc. Pre-NSPS) | 108 | 275 | 93% |  |  |  | Colorado | CO |  | California | California | HICC Oahu | HICC Oahu | Northeast Power Coordinating Council | Northeast Power Coordinating Council | Newfoundland
Natural Gas Consumption (MMBtu/yr) |  |  | 36086.4771 | 57048.5329 |  | 55890.2656 | 33210 |  |  | 6 | CO | 19872.6 | 428759600.787 | 54418479.931 | 30470.565 | 19169.741 | 39953305.881 | 1.12 | 0.705 | 1468.373 | 0.142 | 0.138 | 0.089 | 186.367 | 1.404 | 0.898 | 1874.198 | 0.14 | 0.09 | 187.236 | 29948675.007 | 6974.505 | 12679439.377 | 0 | 55.034 | 0.012816 | 23.2999 | 0 | 78.7431 | 7878.9338 | 10005.8758 | Newfoundland | 20.4 | 21 | 44.9743 | 46.2971 | 2.941% | Nova Scotia | 65035.813 | 18433.8798 | 143379254.0755 | 40639700.1778 | 11400 | 12.5771 | 3.5649 | Nova Scotia | 1582.9203 | 3.5649 | 12.5771 | 5979 | CO | 1468.373 | 0.705 | 1.12 | 7878.9338 | NOx (Large Wall-Fired Unc. Post-NSPS) | 13 | 192 | 36% |  |  |  | Connecticut | CT |  | Colorado | Colorado | MRO East | MRO East | Reliability First Corporation | Reliability First Corporation | Nova Scotia
[10 empty] | 7 | CT | 11788.5 | 161091277.046 | 36496559.656 | 5854.163 | 635.03 | 9096160.084 | 0.321 | 0.035 | 498.467 | 0.073 | 0.076 | 0.008 | 112.932 | 0.266 | 0.046 | 880.139 | 0.036 | 0.006 | 119.335 | 177370.48 | 91734.541 | 17951503.428 | 0 | 0.48599 | 0.25135 | 49.1868 | 0 | 53.8519 | 4413.8757 | 8196.3292 | Nova Scotia | 718 | 770 | 1582.9203 | 1697.5608 | 7.242% | Ontario | 11970.5578 | 18987.8767 | 26390531.0937 | 41861052.725 | 151000 | 0.17477 | 0.27723 | Ontario | 216.0532 | 0.27723 | 0.17477 | 2686 | CT | 498.467 | 0.035 | 0.321 | 4413.8757 | NOx (Tangential-Unc.) | 62 | 167 | 37% |  |  |  | District of Columbia | DC | No used: | Connecticut | Connecticut | MRO West | MRO West | SERC Reliability Corporation | SERC Reliability Corporation | Ontario
Propane Consumption (gal/yr) | [9 empty] | 8 | DC | 24.9 | 763190.852 | 76473.999 | 175.036 | 3.753 | 18422.038 | 4.578 | 0.098 | 481.786 | 0.459 | 0.448 | 0.01 | 48.276 | 3.997 | 0.194 | 1555.026 | 0.3 | 0.015 | 116.889 | 0 | 1000.597 | 22702.026 | 0 | 0 | 1.3084 | 29.6859 | 0 | 100 | 9979.7429 | 9979.7428 | Ontario | 98 | 110 | 216.0532 | 242.5087 | 12.24% | Prince Edward Island | 65.63 | 26.841 | 144689.2106 | 59174.2054 | 492 | 0.29408 | 0.12027 | Prince Edward Island | 4.2329 | 0.12027 | 0.29408 | 7864 | DC | 481.786 | 0.098 | 4.578 | 9979.7429 | NOx (Tangential-FGR) | 8 | 76 | 64% |  |  |  | Delaware | DE | eGRID US Average All Sources | District of Columbia | District of Columbia | NPCC Long Island | NPCC Long Island | Southwest Power Pool | Southwest Power Pool | Prince Edward Island
[10 empty] | 9 | DE | 4010.7 | 63609070.282 | 8731261.003 | 1731.872 | 526.433 | 3874126.143 | 0.397 | 0.121 | 887.415 | 0.054 | 0.052 | 0.017 | 121.81 | 0.333 | 0.14 | 1039.965 | 0.039 | 0.017 | 123.116 | 479349.83 | 62571.361 | 7787468.538 | 277477.31 | 5.49 | 0.71664 | 89.1907 | 3.178 | 99.354 | 7285.21 | 7332.581 | Prince Edward Island | 1.92 | 2.04 | 4.2329 | 4.4974 | 6.25% | Quebec | 1622.9466 | 8275.0073 | 3577980.6215 | 18243246.6986 | 177000 | 0.020215 | 0.10307 | Quebec | 4.4092 | 0.10307 | 0.020215 | 101 | DE | 887.415 | 0.121 | 0.397 | 7285.21 | [7 empty] | Florida | FL | eGrid Subregions Ave All Sources | Delaware | Delaware | NPCC New England | NPCC New England | Texas Regional Entity | Texas Regional Entity | Quebec
Heating Oil Consumption (gal/yr) | [9 empty] | 10 | FL | 100751.4 | 1743606598.221 | 238226428.16 | 65083.285 | 44555.072 | 121996344.001 | 0.546 | 0.374 | 1024.205 | 0.075 | 0.074 | 0.051 | 139.936 | 0.537 | 0.421 | 1193.349 | 0.065 | 0.051 | 144.396 | 39429467.861 | 2820303.253 | 158459723.185 | 23789.858 | 16.5513 | 1.1839 | 66.5164 | 0.0099862 | 87.5251 | 7319.1149 | 8362.3058 | Quebec | 2 | 2 | 4.4092 | 4.4092 | 0% | Saskatchewan | 91918.9566 | 36803.7299 | 202646370.1187 | 81138239.0722 | 20800 | 9.7426 | 3.9009 | Saskatchewan | 1642.4452 | 3.9009 | 9.7426 | 5711 | FL | 1024.205 | 0.374 | 0.546 | 7319.1149 | [7 empty] | Georgia | GA | NERC Average All Sources | Florida | Florida | NPCC NYC/Westchester | NPCC NYC/Westchester | Western Electricity Coordinating Council | Western Electricity Coordinating Council | Saskatchewan
[10 empty] | 11 | GA | 51336.4 | 843098444.075 | 132902274.317 | 29621.082 | 23887.21 | 66567670.523 | 0.446 | 0.359 | 1001.754 | 0.07 | 0.049 | 0.057 | 157.912 | 0.575 | 0.411 | 1464.213 | 0.064 | 0.046 | 164.165 | 37890474.962 | 211845.451 | 52862464.666 | 97549.43 | 28.51 | 0.1594 | 39.7754 | 0.073399 | 71.962 | 6343.7473 | 8815.4086 | Saskatchewan | 745 | 790 | 1642.4452 | 1741.6533 | 6.04% | [13 empty] | GA | 1001.754 | 0.359 | 0.446 | 6343.7473 | [7 empty] | Hawaii | HI | NERC Average Fossil | Georgia | Georgia | NPCC Upstate NY | NPCC Upstate NY
Emissions Profile | US Average Fossil | [8 empty] | 12 | HI | 3501.8 | 92598221.117 | 9948844.667 | 22344.851 | 37331.598 | 7571577.478 | 4.492 | 7.505 | 1522.102 | 0.483 | 0.461 | 0.806 | 163.536 | 5.084 | 8.905 | 1721.957 | 0.509 | 0.891 | 172.262 | 1497379.514 | 6640316.096 | 0 | 63380.048 | 15.0508 | 66.7446 | 0 | 0.63706 | 89.1587 | 9307.4346 | 10439.1823 | [6 empty] | 1 2011 metric tons, taken from National Pollutant Release Inventory (NPRI) Downloadable Datasets, 2011 Air Pollutant Emission Summaries and Trends. 2011 Emissions from Electric Power Generation (Utilities) | [7 empty] | 1 2011 CO2 Emission Rate taken from National Inventory Report, Greenhouse Gas Sources and Sinks in Canada 1990-2011, Environment Canada, Part 3. Generation Intensity (g CO2 eq / kWh) |  |  |  |  | HI | 1522.102 | 7.505 | 4.492 | 9307.4346 | [7 empty] | Iowa | IA |  | Hawaii | Hawaii | RFC East | RFC East
[10 empty] | 13 | IA | 22303.9 | 271381540.06 | 54396530.724 | 21001.212 | 28502.432 | 27140014.842 | 0.772 | 1.048 | 997.858 | 0.155 | 0.153 | 0.21 | 200.014 | 1.392 | 1.998 | 1904.19 | 0.147 | 0.211 | 201.273 | 25198347.051 | 277772.706 | 2960946.967 | 12121.328 | 46.3234 | 0.51064 | 5.4433 | 0.022283 | 52.7624 | 4988.9494 | 9455.5054 | 1 Losses include transmission line losses, metering differences, and other losses | [5 empty] | http://www.ec.gc.ca/inrp-npri/default.asp?lang=en&n=0EC58C98-#Emission_Summaries | [7 empty] | 2 NOX and SOX Emissions taken from National Pollutant Release Inventory (NPRI) Downloadable Datasets, 2011 Air Pollutant Emission Summaries and Trends. 2011 Emissions from Electric Power Generation (Utilities) |  |  |  |  | IA | 997.858 | 1.048 | 0.772 | 4988.9494 | [7 empty] | Idaho | ID |  | Iowa | Iowa | RFC Michigan | RFC Michigan
[10 empty] | 14 | ID | 6212.4 | 28060257.85 | 15660938.441 | 2089.778 | 521.425 | 1477571.885 | 0.267 | 0.067 | 188.695 | 0.149 | 0.131 | 0.037 | 105.314 | 0.224 | 0.043 | 886.061 | 0.03 | 0.006 | 119.317 | 29188.262 | 183.345 | 3321462.369 | 0 | 0.18638 | 0.0011707 | 21.2086 | 0 | 25.2057 | 1791.7354 | 7108.4422 | Source: National Inventory Report, Greenhouse Gas Sources and Sinks in Canada 1990-2011, Environment Canada, Part 3. | [5 empty] | 2 2011 Generation, taken from National Inventory Report, Greenhouse Gas Sources and Sinks in Canada 1990-2011, Environment Canada, Part 3 | [7 empty] | http://www.ec.gc.ca/inrp-npri/default.asp?lang=en&n=0EC58C98-#Emission_Summaries |  |  |  |  | ID | 188.695 | 0.067 | 0.267 | 1791.7354 | [7 empty] | Illinois | IL |  | Idaho | Idaho | RFC West | RFC West
Region | US Average | N | [7 empty] | 15 | IL | 62747.6 | 797823138.821 | 187437381.035 | 33485.631 | 89395.876 | 76035677.094 | 0.357 | 0.954 | 811.318 | 0.084 | 0.083 | 0.224 | 190.608 | 0.808 | 2.313 | 1970.076 | 0.079 | 0.226 | 192.197 | 59337801.513 | 69502.968 | 17480438.763 | 207080.213 | 31.6574 | 0.037081 | 9.326 | 0.11048 | 41.606 | 4256.4783 | 10230.4343 | [14 empty] | 3 SOX emissions used to estimate SO2 emissions |  |  |  |  | IL | 811.318 | 0.954 | 0.357 | 4256.4783 | [7 empty] | Indiana | IN |  | Illinois | Illinois | SERC Midwest | SERC Midwest
[10 empty] | 16 | IN | 40933.2 | 955299879.284 | 101397209.392 | 86575.794 | 87846.778 | 91901514.975 | 1.708 | 1.733 | 1812.703 | 0.181 | 0.17 | 0.184 | 192.403 | 1.762 | 1.887 | 1965.829 | 0.174 | 0.186 | 194.02 | 72533080.112 | 610407.243 | 19995659.487 | 2272492.22 | 71.2792 | 0.59986 | 19.65 | 2.2332 | 94.5444 | 9421.3626 | 9929.5802 | [19 empty] | IN | 1812.703 | 1.733 | 1.708 | 9421.3626 | [7 empty] | Kansas | KS |  | Indiana | Indiana | SERC Mississippi Valley | SERC Mississippi Valley
[10 empty] | 17 | KS | 19888.2 | 281254620.544 | 47599990.322 | 18062.441 | 7160.113 | 28454163.081 | 0.759 | 0.301 | 1195.553 | 0.128 | 0.135 | 0.051 | 202.337 | 1.401 | 0.568 | 2262.592 | 0.126 | 0.051 | 202.835 | 23096063.875 | 28323.68 | 2027207.035 | 0 | 48.5212 | 0.059504 | 4.2588 | 0 | 52.9631 | 5908.7117 | 11156.2812 | [19 empty] | KS | 1195.553 | 0.301 | 0.759 | 5908.7117 | [7 empty] | Kentucky | KY |  | Kansas | Kansas | SERC South | SERC South
Annual Results |  | Reference | Comparison Cases | [6 empty] | 18 | KY | 31178.5 | 794709066.636 | 80273501.005 | 58526.308 | 76475.365 | 78439289.928 | 1.458 | 1.905 | 1954.301 | 0.147 | 0.144 | 0.192 | 197.404 | 1.507 | 1.992 | 2055.81 | 0.145 | 0.192 | 198.228 | 66822058.103 | 1218413.601 | 8228521.283 | 49951.222 | 83.243 | 1.5178 | 10.2506 | 0.062226 | 95.6528 | 9900.0175 | 10349.9523 | [19 empty] | KY | 1954.301 | 1.905 | 1.458 | 9900.0175 | [7 empty] | Louisiana | LA |  | Kentucky | Kentucky | SERC Tennessee Valley | SERC Tennessee Valley
| Units | Case | Recip | Micro Turbine |  | Gas Turbine | Fuel Cell | #5 | #6 | 19 | LA | 36571.7 | 682130857.83 | 106842115.053 | 43819.797 | 38596.775 | 46949097.206 | 0.82 | 0.723 | 878.85 | 0.128 | 0.135 | 0.113 | 137.654 | 1.029 | 0.871 | 1113.707 | 0.131 | 0.111 | 141.707 | 12013648.95 | 4819224.627 | 66052454.521 | 2131813.433 | 11.2443 | 4.5106 | 61.8225 | 1.9953 | 82.9142 | 6384.4754 | 7700.1004 | [19 empty] | LA | 878.85 | 0.723 | 0.82 | 6384.4754 | [7 empty] | Massachusetts | MA |  | Louisiana | Louisiana | SERC Virginia/Carolina | SERC Virginia/Carolina
Energy Consumption | [9 empty] | 20 | MA | 19517.4 | 214741474.293 | 31951671.137 | 8347.816 | 3624.587 | 13121388.574 | 0.523 | 0.227 | 821.327 | 0.078 | 0.065 | 0.034 | 122.206 | 0.283 | 0.154 | 989.178 | 0.037 | 0.02 | 129.495 | 1874931.7 | 422281.087 | 21143936.339 | 527.713 | 5.868 | 1.3216 | 66.1747 | 0.0016516 | 79.8182 | 6720.8214 | 8420.1664 | [19 empty] | MA | 821.327 | 0.227 | 0.523 | 6720.8214 | [7 empty] | Maryland | MD |  | Massachusetts | Massachusetts | SPP North | SPP North
Electricity (generated at central power plant) |  | 75227.6396 | 0 | 0 |  | 0 | 0 | 0 | 0 | 21 | MD | 18265.2 | 213465642.215 | 37166746.524 | 11547.907 | 17541.496 | 18819050.944 | 0.621 | 0.944 | 1012.682 | 0.108 | 0.104 | 0.164 | 176.319 | 0.982 | 1.707 | 1901.952 | 0.094 | 0.163 | 181.384 | 13826213.23 | 160608.876 | 5423046.323 | 0 | 37.1992 | 0.43212 | 14.5906 | 0 | 54.5592 | 5743.4579 | 10526.6401 | [19 empty] | MD | 1012.682 | 0.944 | 0.621 | 5743.4579 | [7 empty] | Maine | ME |  | Maryland | Maryland | SPP South | SPP South
Natural Gas |  | 0 | 36086.4771 | 57048.5329 |  | 55890.2656 | 33210 | 0 | 0 | 22 | ME | 5717.6 | 58575396.805 | 11514427.426 | 3326.365 | 1666.405 | 1939972.213 | 0.578 | 0.289 | 336.964 | 0.114 | 0.104 | 0.057 | 66.238 | 0.181 | 0.208 | 850.006 | 0.026 | 0.03 | 121.155 | 69823.097 | 109781.494 | 3498481.826 | 148580.065 | 0.6064 | 0.95343 | 30.3835 | 1.2904 | 59.4701 | 5087.1307 | 8554.1044 | [19 empty] | ME | 336.964 | 0.289 | 0.578 | 5087.1307 | [7 empty] | Michigan | MI |  | Maine | Maine | WECC California | WECC California
Propane | MMBtu/yr | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 23 | MI | 36977.2 | 716544288.999 | 112121789.925 | 46617.641 | 86271.432 | 61658803.317 | 0.832 | 1.539 | 1099.854 | 0.13 | 0.123 | 0.241 | 172.1 | 1.104 | 2.329 | 1699.032 | 0.116 | 0.245 | 178.84 | 40526872.819 | 818978.892 | 29295153.906 | 1774317.299 | 36.1454 | 0.73044 | 26.128 | 1.5825 | 66.9382 | 6390.7675 | 9547.2589 | [19 empty] | MI | 1099.854 | 1.539 | 0.832 | 6390.7675 | [7 empty] | Minnesota | MN |  | Michigan | Michigan | WECC Northwest | WECC Northwest
Heating Oil |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 24 | MN | 21832.4 | 341048055.773 | 60036475.896 | 20098.494 | 17474.221 | 30398578.571 | 0.67 | 0.582 | 1012.67 | 0.118 | 0.11 | 0.102 | 178.266 | 1.033 | 0.987 | 1853.687 | 0.106 | 0.101 | 190.095 | 23206288.695 | 30705.379 | 8929397.953 | 0 | 38.6537 | 0.051145 | 14.8733 | 0 | 57.4082 | 5680.6808 | 9895.2484 | [19 empty] | MN | 1012.67 | 0.582 | 0.67 | 5680.6808 | [7 empty] | Missouri | MO |  | Minnesota | Minnesota | WECC Rockies | WECC Rockies
Total Energy Consumption |  | 75227.6396 | 36086.4771 | 57048.5329 |  | 55890.2656 | 33210 | 0 | 0 | 25 | MO | 24747.7 | 654674531.253 | 78611512.544 | 57269.33 | 100046.936 | 66337989.476 | 1.457 | 2.545 | 1687.742 | 0.175 | 0.166 | 0.306 | 202.659 | 1.707 | 2.992 | 1998.954 | 0.173 | 0.304 | 203.07 | 60321889.5 | 73789.774 | 6035794.364 | 8979.192 | 76.7342 | 0.093866 | 7.678 | 0.011422 | 84.6938 | 8327.9727 | 9833.0348 | [19 empty] | MO | 1687.742 | 2.545 | 1.457 | 8327.9727 | [7 empty] | Mississippi | MS |  | Missouri | Missouri | WECC Southwest | WECC Southwest
CO2 Emissions | lb/year | [59 empty] | MS | 940.716 | 0.162 | 0.428 | 7258.5792 | [7 empty] | Montana | MT |  | Mississippi | Mississippi
Electricity |  | 13510472.1527 | 0 | 0 |  | 0 | 0 | 0 | 0 | 26 | MS | 19599.7 | 456428857.875 | 62881294.963 | 13464.768 | 5081.933 | 29576726.266 | 0.428 | 0.162 | 940.716 | 0.059 | 0.068 | 0.022 | 129.601 | 0.474 | 0.129 | 1060.249 | 0.059 | 0.016 | 131.479 | 5342026.01 | 17785.283 | 50094738.667 | 5272.354 | 8.4954 | 0.028284 | 79.6656 | 0.0083846 | 90.6216 | 7258.5792 | 8009.769 | [19 empty] | MT | 1251.022 | 1.022 | 1.123 | 6046.7974 | [7 empty] | North Carolina | NC |  | Montana | Montana
Natural Gas |  | 0 | 4245467.8933 | 6711592.1053 |  | 6575325.3632 | 3907058.8235 | 0 | 0 | 27 | MT | 7258.5 | 168001376.728 | 27783529.992 | 15603.434 | 14192.894 | 17378904.074 | 1.123 | 1.022 | 1251.022 | 0.186 | 0.193 | 0.169 | 206.89 | 2.049 | 1.866 | 2284.625 | 0.186 | 0.169 | 207.072 | 14269221.559 | 459922.71 | 476060.668 | 8585.72 | 51.3586 | 1.6554 | 1.7135 | 0.030902 | 56.0073 | 6046.7974 | 10796.4426 | [19 empty] | NC | 867.441 | 0.445 | 0.558 | 5386.1171 | [7 empty] | North Dakota | ND |  | North Carolina | North Carolina
Propane |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 28 | NC | 48223.6 | 704332577.085 | 130768152.699 | 36492.384 | 29106.389 | 56716823.493 | 0.558 | 0.445 | 867.441 | 0.104 | 0.1 | 0.083 | 161.051 | 0.836 | 0.61 | 1462.692 | 0.095 | 0.069 | 165.833 | 37435780.008 | 251193.382 | 39251101.714 | 362939.45 | 28.6276 | 0.19209 | 30.0158 | 0.27754 | 61.2906 | 5386.1171 | 8787.8422 | [19 empty] | ND | 1663.754 | 2.394 | 1.98 | 7788.3908 | [7 empty] | Nebraska | NE |  | North Dakota | North Dakota
Heating Oil |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 29 | ND | 9442.3 | 294840840.947 | 37856451.758 | 37479.177 | 45313.244 | 31491914.605 | 1.98 | 2.394 | 1663.754 | 0.254 | 0.236 | 0.307 | 213.62 | 2.703 | 3.268 | 2271.526 | 0.254 | 0.307 | 213.643 | 26580349.545 | 30102.099 | 1071113.726 | 45969.348 | 70.2135 | 0.079516 | 2.8294 | 0.12143 | 73.3627 | 7788.3908 | 10616.2779 | [19 empty] | NE | 1281.153 | 2.771 | 1.129 | 6203.5513 | [7 empty] | New Hampshire | NH |  | Nebraska | Nebraska
Total CO2 Emissions |  | 13510472.1527 | 4245467.8933 | 6711592.1053 |  | 6575325.3632 | 3907058.8235 | 0 | 0 | 30 | NE | 10004.2 | 230758728.43 | 37197843.2 | 20990.101 | 51539.299 | 23828059.637 | 1.129 | 2.771 | 1281.153 | 0.182 | 0.18 | 0.447 | 206.519 | 1.8 | 4.591 | 2122.981 | 0.176 | 0.448 | 207.203 | 21897715.076 | -17939.889 | 537861.686 | 0 | 58.8399 | 0 | 1.4453 | 0 | 60.4997 | 6203.5513 | 10257.1058 | [19 empty] | NH | 310.564 | 0.079 | 0.236 | 3533.963 | [7 empty] | New Jersey | NJ |  | New Hampshire | New Hampshire
SO2 Emissions | lb/year | [8 empty] | 31 | NH | 4650.3 | 68143617.017 | 19282493.05 | 2270.683 | 759.014 | 2994227.255 | 0.236 | 0.079 | 310.564 | 0.067 | 0.057 | 0.022 | 87.88 | 0.315 | 0.121 | 965.006 | 0.042 | 0.016 | 127.824 | 422017.041 | 38798.353 | 4744436.031 | 0 | 2.1886 | 0.20121 | 24.6049 | 0 | 36.01 | 3533.963 | 9813.8459 | [19 empty] | NJ | 557.822 | 0.054 | 0.235 | 4655.3946 | [7 empty] | New Mexico | NM |  | New Jersey | New Jersey
Electricity |  | 10775.4262 | 0 | 0 |  | 0 | 0 | 0 | 0 | 32 | NJ | 28577 | 361250228.15 | 77598196.669 | 9131.36 | 2080.798 | 21643003.081 | 0.235 | 0.054 | 557.822 | 0.051 | 0.05 | 0.012 | 119.823 | 0.227 | 0.059 | 914.086 | 0.031 | 0.008 | 122.759 | 1314541.066 | 146126.232 | 43807453.226 | 207167.75 | 1.6898 | 0.18784 | 56.313 | 0.26631 | 60.5006 | 4655.3946 | 7675.5548 | [19 empty] | NM | 1572.786 | 0.502 | 2.353 | 8693.4174 | [7 empty] | Nevada | NV |  | New Mexico | New Mexico
Natural Gas |  | 0 | 21.2273 | 33.558 |  | 32.8766 | 19.5353 | 0 | 0 | 33 | NM | 13285.9 | 286209486.338 | 32922552.001 | 38733.952 | 8264.524 | 25890069.925 | 2.353 | 0.502 | 1572.786 | 0.271 | 0.263 | 0.058 | 180.917 | 2.728 | 0.582 | 1823.793 | 0.271 | 0.058 | 180.924 | 18365269.5 | 51682.706 | 9957552.879 | 0 | 55.7833 | 0.15698 | 30.2454 | 0 | 86.2406 | 8693.4174 | 10080.4263 | [19 empty] | NV | 769.912 | 0.159 | 0.477 | 6005.2409 | [7 empty] | New York | NY |  | Nevada | Nevada
Propane |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 34 | NV | 19953.8 | 235577759.367 | 39228694.003 | 9361.941 | 3118.066 | 15101320.561 | 0.477 | 0.159 | 769.912 | 0.079 | 0.085 | 0.026 | 128.207 | 0.586 | 0.174 | 962.473 | 0.078 | 0.023 | 128.054 | 2166830.74 | 10985.185 | 28921611.617 | 742.456 | 5.5236 | 0.028003 | 73.7257 | 0.0018926 | 79.4736 | 6005.2409 | 7556.2698 | [19 empty] | NY | 464.02 | 0.137 | 0.341 | 3940.4088 | [7 empty] | Ohio | OH |  | New York | New York
Heating Oil |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 35 | NY | 51335.7 | 528372701.083 | 134090832.639 | 22846.976 | 9164.012 | 31110393.202 | 0.341 | 0.137 | 464.02 | 0.086 | 0.084 | 0.035 | 117.759 | 0.446 | 0.295 | 1000.197 | 0.055 | 0.036 | 122.52 | 1770237.86 | 639490.033 | 56470523.809 | 0 | 1.3202 | 0.47691 | 42.1136 | 0 | 46.2543 | 3940.4088 | 8519.0145 | [19 empty] | OH | 1465.96 | 1.786 | 1.007 | 7991.9906 | [7 empty] | Oklahoma | OK |  | Ohio | Ohio
Total SO2 Emissions |  | 10775.4262 | 21.2273 | 33.558 |  | 32.8766 | 19.5353 | 0 | 0 | 36 | OH | 46930.8 | 950424128.328 | 118922077.758 | 59879.582 | 106170.308 | 87167527.924 | 1.007 | 1.786 | 1465.96 | 0.126 | 0.122 | 0.223 | 183.429 | 1.116 | 2.131 | 1753.902 | 0.118 | 0.225 | 184.873 | 68775163.651 | 1181963.453 | 28941686.826 | 732619.709 | 57.8029 | 0.9934 | 24.3244 | 0.61574 | 84.2929 | 7991.9906 | 9476.4302 | [19 empty] | OK | 1043.716 | 1.276 | 0.691 | 6657.6883 | [7 empty] | Oregon | OR |  | Oklahoma | Oklahoma
NOX Emissions | lb/year | [8 empty] | 37 | OK | 33525.2 | 523660527.977 | 78655008.003 | 27175.231 | 50195.656 | 41046732.231 | 0.691 | 1.276 | 1043.716 | 0.104 | 0.106 | 0.192 | 156.768 | 0.969 | 1.789 | 1474.508 | 0.103 | 0.191 | 157.484 | 19158044.292 | 17261.291 | 36529085.696 | 22274.728 | 24.3571 | 0.021946 | 46.4422 | 0.02832 | 71.3171 | 6657.6883 | 9335.3296 | [19 empty] | OR | 305.891 | 0.139 | 0.352 | 2545.2692 | [7 empty] | Pennsylvania | PA |  | Oregon | Oregon
Electricity |  | 12488.2023 | 0 | 0 |  | 0 | 0 | 0 | 0 | 38 | OR | 19278.2 | 153178914.871 | 60181811.826 | 10598.563 | 4192.085 | 9204524.036 | 0.352 | 0.139 | 305.891 | 0.138 | 0.149 | 0.055 | 120.18 | 0.85 | 0.437 | 1062.003 | 0.103 | 0.053 | 128.819 | 1898202.1 | 4849.88 | 15306661.154 | 0 | 3.1541 | 0.0080587 | 25.4338 | 0 | 30.3257 | 2545.2692 | 8393.0521 | [19 empty] | PA | 855.444 | 0.959 | 0.821 | 5279.9354 | [7 empty] | Rhode Island | RI |  | Pennsylvania | Pennsylvania
Natural Gas |  | 0 | 4453.8103 | 7040.9573 |  | 6898.0034 | 4098.7941 | 0 | 0 | 39 | PA | 68558.5 | 1135537271.059 | 215066508.488 | 88300.604 | 103118.005 | 91988694.244 | 0.821 | 0.959 | 855.444 | 0.156 | 0.137 | 0.182 | 162.018 | 1.291 | 1.613 | 1467.227 | 0.147 | 0.183 | 166.568 | 54672029.679 | 362714.597 | 68049155.341 | 537394.297 | 25.421 | 0.16865 | 31.641 | 0.24987 | 58.9486 | 5279.9354 | 8956.8414 | [19 empty] | RI | 870.822 | 0.023 | 0.244 | 7618.5543 | [7 empty] | South Carolina | SC |  | Rhode Island | Rhode Island
Propane |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 40 | RI | 2398 | 50014933.405 | 6564885.1 | 801.215 | 75.385 | 2858423.741 | 0.244 | 0.023 | 870.822 | 0.032 | 0.025 | 0.003 | 114.303 | 0.214 | 0.013 | 905.025 | 0.028 | 0.002 | 119.116 | 0 | 26282.811 | 6290503.203 | 0 | 0 | 0.40035 | 95.8205 | 0 | 99.3401 | 7618.5543 | 7669.1646 | [19 empty] | SC | 629.428 | 0.24 | 0.282 | 3838.4857 | [7 empty] | South Dakota | SD |  | South Carolina | South Carolina
Heating Oil |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 41 | SC | 31484.7 | 372278468.671 | 96985763.86 | 13683.385 | 11636.435 | 30522786.49 | 0.282 | 0.24 | 629.428 | 0.074 | 0.073 | 0.063 | 163.978 | 0.618 | 0.52 | 1589.85 | 0.066 | 0.056 | 170.546 | 21002913.373 | 113861.869 | 16366854.272 | 45419.605 | 21.6557 | 0.1174 | 16.8755 | 0.046831 | 41.1456 | 3838.4857 | 9329.0243 | [19 empty] | SD | 513.316 | 0.142 | 0.207 | 2790.2422 | [7 empty] | Tennessee | TN |  | South Dakota | South Dakota
Total NOX Emissions |  | 12488.2023 | 4453.8103 | 7040.9573 |  | 6898.0034 | 4098.7941 | 0 | 0 | 42 | SD | 5438 | 28709961.454 | 10289415.719 | 1062.629 | 729.414 | 2640861.381 | 0.207 | 0.142 | 513.316 | 0.074 | 0.076 | 0.051 | 183.968 | 0.707 | 0.486 | 1758.21 | 0.074 | 0.051 | 183.968 | 2082680.5 | 2792.845 | 918561.385 | 0 | 20.241 | 0.027143 | 8.9272 | 0 | 29.1954 | 2790.2422 | 9557.1337 | [19 empty] | TN | 992.271 | 0.803 | 0.513 | 5311.1831 | [7 empty] | Texas | TX |  | Tennessee | Tennessee
Emissions Savings (relative to Reference Case) | [9 empty] | 43 | TN | 27972.7 | 421392634.041 | 79340633.31 | 20342.043 | 31860.901 | 39363687.712 | 0.513 | 0.803 | 992.271 | 0.097 | 0.094 | 0.151 | 186.827 | 0.913 | 1.454 | 1831.783 | 0.094 | 0.15 | 188.671 | 31167633.516 | 121581.46 | 11318514.75 | 34302.144 | 39.2833 | 0.15324 | 14.2657 | 0.043234 | 54.9228 | 5311.1831 | 9670.2766 | [19 empty] | TX | 1049.527 | 1.09 | 0.605 | 6576.1454 | [7 empty] | Utah | UT |  | Texas | Texas
CO2 | lb/year | N/A | 9265004.2594 | 6798880.0475 |  | 6935146.7895 | 9603413.3292 | 13510472.1527 | 13510472.1527 | 44 | TX | 182433.5 | 2985184261.847 | 453941342.056 | 137386.615 | 247401.257 | 238211887.056 | 0.605 | 1.09 | 1049.527 | 0.092 | 0.091 | 0.166 | 159.596 | 0.757 | 1.406 | 1360.568 | 0.089 | 0.166 | 160.448 | 121230932.59 | 196421.938 | 225976260.44 | 2516118.132 | 26.7063 | 0.04327 | 49.7809 | 0.55428 | 77.6 | 6576.1454 | 8474.4186 | [19 empty] | UT | 1627.372 | 0.878 | 1.777 | 8686.5934 | [7 empty] | Virginia | VA |  | Utah | Utah
|  |  | 68.58% | 50.32% |  | 51.33% | 71.08% | 100% | 100% | 45 | UT | 11043.7 | 331253925.886 | 38133928.003 | 33873.88 | 16749.524 | 31029038.987 | 1.777 | 0.878 | 1627.372 | 0.205 | 0.197 | 0.101 | 187.343 | 1.897 | 0.952 | 1777.411 | 0.2 | 0.101 | 187.772 | 25939443.13 | 31552.02 | 8691320.105 | 54099.063 | 68.022 | 0.08274 | 22.7916 | 0.14187 | 91.8168 | 8686.5934 | 9460.7895 | [19 empty] | VA | 813.802 | 0.255 | 0.557 | 5908.226 | [7 empty] | Vermont | VT |  | Virginia | Virginia
SO2 |  | N/A | 10754.1989 | 10741.8683 |  | 10742.5496 | 10755.8909 | 10775.4262 | 10775.4262 | 46 | VA | 34581.2 | 546834777.577 | 92554816.451 | 25776.56 | 11804.945 | 37660633.018 | 0.557 | 0.255 | 813.802 | 0.094 | 0.088 | 0.043 | 137.74 | 0.634 | 0.353 | 1243.007 | 0.075 | 0.042 | 146.858 | 16499412.338 | 535360.843 | 40904843.159 | 0 | 17.8266 | 0.57843 | 44.1953 | 0 | 67.5202 | 5908.226 | 8750.3102 | [19 empty] | VT | 56.89 | 0.013 | 0.356 | 2625.7555 | [7 empty] | Washington | WA |  | Vermont | Vermont
|  |  | 99.8% | 99.69% |  | 99.69% | 99.82% | 100% | 100% | 47 | VT | 796.3 | 5018362.576 | 1911207.085 | 340.023 | 12.435 | 54363.959 | 0.356 | 0.013 | 56.89 | 0.136 | 0.134 | 0.005 | 21.666 | 8.495 | 4.122 | 3251.2 | 0.425 | 0.206 | 162.655 | 0 | 4016.739 | 1965.432 | 0 | 0 | 0.21017 | 0.10284 | 0 | 25.2969 | 2625.7555 | 10379.7318 | [19 empty] | WA | 186.844 | 0.05 | 0.149 | 1355.0482 | [7 empty] | Wisconsin | WI |  | Washington | Washington
NOX |  | N/A | 8034.392 | 5447.245 |  | 5590.1989 | 8389.4082 | 12488.2023 | 12488.2023 | 48 | WA | 34016.1 | 154592822.317 | 114086582.682 | 8506.671 | 2840.859 | 10658190.065 | 0.149 | 0.05 | 186.844 | 0.11 | 0.106 | 0.037 | 137.887 | 0.815 | 0.187 | 1319.577 | 0.095 | 0.022 | 154.336 | 4601726.271 | 21965.243 | 10982248.227 | 401642.3 | 4.0335 | 0.019253 | 9.6262 | 0.35205 | 15.8431 | 1355.0482 | 8552.9028 | [19 empty] | WI | 1388.88 | 0.504 | 0.673 | 7611.2474 | [7 empty] | West Virginia | WV |  | Wisconsin | Wisconsin
|  |  | 64.34% | 43.62% |  | 44.76% | 67.18% | 100% | 100% | 49 | WI | 23413.6 | 494476945.406 | 64966610.542 | 21867.293 | 16381.658 | 45115418.818 | 0.673 | 0.504 | 1388.88 | 0.088 | 0.087 | 0.066 | 182.477 | 0.688 | 0.627 | 1838.705 | 0.07 | 0.064 | 187.731 | 33362840.597 | 147111.25 | 15472759.274 | 7167.538 | 51.3538 | 0.22644 | 23.8165 | 0.011033 | 77.7354 | 7611.2474 | 9791.2296 | [19 empty] | WV | 1975.757 | 1.181 | 1.33 | 9643.6201 | [7 empty] | Wyoming | WY |  | West Virginia | West Virginia
Equivalent CO2 Emissions | [9 empty] | 50 | WV | 20625.5 | 732365129.682 | 75942967.562 | 50512.838 | 44840.323 | 75022430.97 | 1.33 | 1.181 | 1975.757 | 0.138 | 0.131 | 0.122 | 204.877 | 1.386 | 1.23 | 2058.656 | 0.138 | 0.122 | 204.877 | 71512961.29 | 122668.761 | 1224566.665 | 24651.155 | 94.1514 | 0.1615 | 1.6122 | 0.032455 | 95.9414 | 9643.6201 | 10049.9428 | [19 empty] | WY | 2026.26 | 1.394 | 1.58 | 9738.3928 | [7 empty] | ASCC Alaska Grid | ASCC Alaska Grid |  | Wyoming | Wyoming
Cars |  | N/A | 888.4944 | 651.9983 |  | 665.066 | 920.9471 | 1295.6258 | 1295.6258 | 51 | WY | 13744.3 | 454360590.958 | 46656629.978 | 36847.688 | 32523.13 | 47269240.574 | 1.58 | 1.394 | 2026.26 | 0.162 | 0.164 | 0.143 | 208.069 | 1.823 | 1.609 | 2324.747 | 0.164 | 0.145 | 209.252 | 40026874.24 | 55635.566 | 788142.618 | 358138.316 | 85.7903 | 0.11924 | 1.6892 | 0.7676 | 88.5058 | 9738.3928 | 11003.1178 | [19 empty] | US Average_Fossil | 1565.2376 | 1.2484 | 1.4468 | 8715.3973 | [7 empty] | ASCC Miscellaneous | ASCC Miscellaneous
Homes |  | N/A | 620.5816 | 455.3975 |  | 464.5248 | 643.2486 | 904.9483 | 904.9483 | 52 | ASCC Alaska Grid | 2406.1 | 37034855.156 | 4705315.769 | 15338.096 | 1235.068 | 2522706.992 | 6.519 | 0.525 | 1072.28 | 0.828 | 0.832 | 0.067 | 136.234 | 7.658 | 0.624 | 1281.606 | 0.823 | 0.067 | 137.739 | 594138.933 | 430960.626 | 2911689.364 | 0 | 12.627 | 9.159 | 61.8808 | 0 | 84.5196 | 7870.8544 | 9312.4659 | [19 empty] | AK_Fossil | 1311.311 | 0.778 | 9.265 | 9442.4321 | [7 empty] | WECC Southwest | WECC Southwest
[10 empty] | 53 | ASCC Miscellaneous | 1033.2 | 5518225.472 | 1629717.742 | 5670.039 | 513.397 | 409975.552 | 6.958 | 0.63 | 503.125 | 2.055 | 1.938 | 0.186 | 148.59 | 21.126 | 1.913 | 1530.678 | 2.05 | 0.186 | 148.524 | 0 | 400369.021 | 128797.939 | 0 | 0 | 24.5668 | 7.9031 | 0 | 32.5006 | 3386.0007 | 10418.2578 | [19 empty] | AL_Fossil | 1404.737 | 0.557 | 0.604 | 8635.3626 | [7 empty] | WECC California | WECC California
[10 empty] | 54 | WECC Southwest | 63308.3 | 1060149568.706 | 166327576.054 | 79933.546 | 22958.347 | 86793512.03 | 0.961 | 0.276 | 1043.645 | 0.151 | 0.138 | 0.043 | 163.738 | 1.364 | 0.371 | 1497 | 0.15 | 0.041 | 164.843 | 49085178.17 | 104448.564 | 66277483.534 | 742.456 | 29.511 | 0.062797 | 39.8474 | 0.00044638 | 69.806 | 6373.8653 | 9130.7935 | [19 empty] | AR_Fossil | 1611.949 | 2.235 | 1.29 | 8934.2389 | [7 empty] | ERCOT All | ERCOT All
Assumptions and Data Sources | [9 empty] | 55 | WECC California | 110655.6 | 884398707.026 | 200602485.031 | 56897.036 | 5192.553 | 52945255.059 | 0.567 | 0.052 | 527.862 | 0.129 | 0.125 | 0.012 | 119.732 | 0.79 | 0.061 | 956.99 | 0.105 | 0.008 | 126.856 | 8709846.815 | 187090.047 | 97097196.554 | 1426815.666 | 4.3418 | 0.093264 | 48.4028 | 0.71127 | 56.6441 | 4408.7126 | 7783.1875 | [19 empty] | AZ_Fossil | 1567.773 | 0.399 | 1.034 | 9295.8813 | [7 empty] | FRCC All | FRCC All
[10 empty] | 56 | ERCOT All | 159336.3 | 2454551297.903 | 389939061.959 | 106194.764 | 201831.991 | 196754748.55 | 0.545 | 1.035 | 1009.156 | 0.087 | 0.085 | 0.164 | 160.318 | 0.699 | 1.382 | 1351.141 | 0.083 | 0.165 | 161.098 | 101006612.69 | 178137.041 | 187922725.435 | 1838398.994 | 25.9032 | 0.045683 | 48.1928 | 0.47146 | 75.0597 | 6294.7048 | 8386.2622 | [19 empty] | CA_Fossil | 867.421 | 0.01 | 0.648 | 7652.2146 | [7 empty] | HICC Miscellaneous | HICC Miscellaneous
Description | Value | Units | Source |  |  | Link |  |  |  | 57 | FRCC All | 97820.3 | 1665956580.815 | 229407929.06 | 61022.225 | 42714.18 | 116043999.116 | 0.532 | 0.372 | 1011.683 | 0.073 | 0.073 | 0.051 | 139.312 | 0.529 | 0.425 | 1183.524 | 0.064 | 0.052 | 143.661 | 36790857.618 | 2814817.331 | 152730470.895 | 19074.17 | 16.0373 | 1.227 | 66.5759 | 0.0083145 | 87.0268 | 7261.9834 | 8344.5409 | [19 empty] | CO_Fossil | 1874.198 | 0.898 | 1.404 | 10005.8758 | [7 empty] | HICC Oahu | HICC Oahu
Average gross (or higher) heating value of natural gas | 1020 | Btu/scf | U.S. Environmental Protection Agency, AP 42, Fifth Edition, Volume I. Chapter 1: External Combustion Sources, Section 4. Natural Gas Combustion, Final Section, Section 1.4.1. |  |  | http://www.epa.gov/ttn/chief/ap42/ch01/final/c01s04.pdf |  |  |  | 58 | HICC Miscellaneous | 1164.1 | 20112676.627 | 2741703.667 | 10206.657 | 6168.214 | 1579243.81 | 7.445 | 4.5 | 1152.016 | 1.015 | 0.996 | 0.613 | 157.04 | 10.913 | 6.588 | 1688.235 | 1.062 | 0.641 | 164.362 | 5525.764 | 1691007.403 | 0 | 0 | 0.20154 | 61.6772 | 0 | 0 | 70.2652 | 7335.8317 | 10440.2001 | [19 empty] | CT_Fossil | 880.139 | 0.046 | 0.266 | 8196.3292 | [7 empty] | MRO East | MRO East
Natural Gas CO2 Emission Factor | 120000 | lb/106 scf | U.S. Environmental Protection Agency, AP 42, Fifth Edition, Volume I. Chapter 1: External Combustion Sources, Section 4. Natural Gas Combustion, Final Section. Table 1.4-2 |  |  | http://www.epa.gov/ttn/chief/ap42/ch01/final/c01s04.pdf |  |  |  | 59 | HICC Oahu | 2337.7 | 72485544.49 | 7207141 | 12138.194 | 31163.384 | 5992333.668 | 3.368 | 8.648 | 1662.888 | 0.335 | 0.319 | 0.86 | 165.339 | 3.412 | 9.57 | 1731.629 | 0.344 | 0.965 | 174.61 | 1491853.75 | 4949308.693 | 0 | 63380.048 | 20.6997 | 68.6723 | 0 | 0.87941 | 96.346 | 10057.4617 | 10438.9 | [19 empty] | DC_Fossil | 1555.026 | 0.194 | 3.997 | 9979.7428 | [7 empty] | MRO West | MRO West
Natural Gas SO2 Emission Factor | 0.6 | lb/106 scf | U.S. Environmental Protection Agency, AP 42, Fifth Edition, Volume I. Chapter 1: External Combustion Sources, Section 4. Natural Gas Combustion, Final Section. Table 1.4-2 |  |  | http://www.epa.gov/ttn/chief/ap42/ch01/final/c01s04.pdf |  |  |  | 60 | MRO East | 11271.2 | 185400680.989 | 20471859.537 | 10709.482 | 13181.802 | 17075701.597 | 1.046 | 1.288 | 1668.212 | 0.116 | 0.114 | 0.142 | 184.203 | 0.98 | 1.392 | 1969.779 | 0.095 | 0.136 | 191.861 | 13210511.573 | 129947.992 | 4206324.625 | 17410.056 | 64.5301 | 0.63476 | 20.5469 | 0.085044 | 91.1992 | 9056.3674 | 9930.3177 | [19 empty] | DE_Fossil | 1039.965 | 0.14 | 0.333 | 7332.581 | [7 empty] | NPCC New England | NPCC New England
Natural Gas NOX Emission Factor | 125.8889 | lb/106 scf | U.S. Environmental Protection Agency, AP 42, Fifth Edition, Volume I. Chapter 1: External Combustion Sources, Section 4. Natural Gas Combustion, Background Document, Table 3.4-1. |  |  | http://www.epa.gov/ttn/chief/ap42/ch01/bgdocs/b01s04.pdf |  |  |  | 61 | MRO West | 74698.1 | 1358775879.289 | 218204106.304 | 113818.445 | 151870.764 | 135157508.596 | 1.043 | 1.392 | 1238.817 | 0.168 | 0.159 | 0.224 | 198.94 | 1.654 | 2.311 | 2068.415 | 0.162 | 0.227 | 203.188 | 115022479.189 | 354561.615 | 14581752.93 | 62940.548 | 52.7133 | 0.16249 | 6.6826 | 0.028845 | 61.0966 | 6227.0867 | 10192.2042 | [19 empty] | FL_Fossil | 1193.349 | 0.421 | 0.537 | 8362.3058 | [7 empty] | WECC Northwest | WECC Northwest
Propane Heat Content | 91.5 | MMBtu/103 gal | U.S. Environmental Protection Agency, AP 42, Fifth Edition, Volume I. Chapter 1: External Combustion Sources, Section 5. Liquefied Petroleum Gas Combustion, Final Document, Table 1.5-1. |  |  | http://www.epa.gov/ttn/chief/ap42/ch01/final/c01s05.pdf |  |  |  | 62 | NPCC New England | 44890.4 | 557588325.143 | 107729043.454 | 20945.493 | 6773.329 | 30064802.374 | 0.389 | 0.126 | 558.156 | 0.075 | 0.067 | 0.024 | 107.839 | 0.267 | 0.104 | 933.923 | 0.036 | 0.014 | 124.474 | 2544142.318 | 693211.025 | 53630826.259 | 149107.778 | 2.3616 | 0.64348 | 49.7831 | 0.13841 | 61.222 | 5175.8403 | 8454.2103 | [19 empty] | GA_Fossil | 1464.213 | 0.411 | 0.575 | 8815.4086 | [7 empty] | NPCC NYC/Westchester | NPCC NYC/Westchester
Propane CO2 Emission Factor | 12500 | lb/103 gal | U.S. Environmental Protection Agency, AP 42, Fifth Edition, Volume I. Chapter 1: External Combustion Sources, Section 5. Liquefied Petroleum Gas Combustion, Final Document, Table 1.5-1. |  |  | http://www.epa.gov/ttn/chief/ap42/ch01/final/c01s05.pdf |  |  |  | 63 | WECC Northwest | 90679.3 | 1070374960.541 | 284912897.14 | 87195.456 | 62608.49 | 92767480.389 | 0.612 | 0.439 | 651.199 | 0.163 | 0.162 | 0.117 | 173.336 | 1.468 | 1.112 | 1706.11 | 0.154 | 0.117 | 179.022 | 64014901.352 | 546885.088 | 43508250.867 | 822465.399 | 22.4682 | 0.19195 | 15.2707 | 0.28867 | 39.6772 | 3756.8498 | 9468.5309 | [19 empty] | HI_Fossil | 1721.957 | 8.905 | 5.084 | 10439.1823 | [7 empty] | NPCC Long Island | NPCC Long Island
Propane SO2 Emission Factor | 0.1 | lb/103 gal | U.S. Environmental Protection Agency, AP 42, Fifth Edition, Volume I. Chapter 1: External Combustion Sources, Section 5. Liquefied Petroleum Gas Combustion, Final Document, Table 1.5-1. |  |  | http://www.epa.gov/ttn/chief/ap42/ch01/final/c01s05.pdf |  |  |  | 64 | NPCC NYC/Westchester | 16614.3 | 238234905.335 | 44416982.224 | 5718.859 | 345.324 | 14120374.062 | 0.258 | 0.016 | 635.81 | 0.048 | 0.054 | 0.003 | 118.542 | 0.324 | 0.016 | 952.759 | 0.04 | 0.002 | 119.181 | 0 | 196126.872 | 28705805.459 | 0 | 0 | 0.44156 | 64.628 | 0 | 65.9416 | 5363.5995 | 8133.8586 | [19 empty] | IA_Fossil | 1904.19 | 1.998 | 1.392 | 9455.5054 | [7 empty] | NPCC Upstate NY | NPCC Upstate NY
Propane NOX Emission Factor | 13 | lb/103 gal | U.S. Environmental Protection Agency, AP 42, Fifth Edition, Volume I. Chapter 1: External Combustion Sources, Section 5. Liquefied Petroleum Gas Combustion, Final Document, Table 1.5-1. |  |  | http://www.epa.gov/ttn/chief/ap42/ch01/final/c01s05.pdf |  |  |  | 65 | NPCC Long Island | 6274.7 | 118422140.025 | 11777168.295 | 5069.889 | 924.398 | 6938646.493 | 0.861 | 0.157 | 1178.322 | 0.086 | 0.081 | 0.016 | 117.185 | 0.632 | 0.16 | 1129.489 | 0.067 | 0.017 | 120.553 | 0 | 318444.563 | 10425354.976 | 0 | 0 | 2.7039 | 88.5217 | 0 | 99.196 | 10055.2303 | 10136.7258 | [19 empty] | ID_Fossil | 886.061 | 0.043 | 0.224 | 7108.4422 | [7 empty] | RFC East | RFC East
Heating Oil (No. 2) Heat Content | 140 | MMBtu/103 gal | U.S. Environmental Protection Agency, AP 42, Fifth Edition, Volume I. Chapter 1: External Combustion Sources, Section 3. Fuel Oil Combustion, Background Document. |  |  | http://www.epa.gov/ttn/chief/ap42/ch01/bgdocs/b01s03.pdf |  |  |  | 66 | NPCC Upstate NY | 30844.4 | 211022137.061 | 84093338.12 | 12356.763 | 7905.498 | 12389521.323 | 0.294 | 0.188 | 294.661 | 0.117 | 0.109 | 0.075 | 117.424 | 0.424 | 0.601 | 947.055 | 0.057 | 0.081 | 126.893 | 1770237.86 | 159964.158 | 23313194.874 | 0 | 2.1051 | 0.19022 | 27.723 | 0 | 32.1784 | 2509.38 | 7798.3463 | [19 empty] | IL_Fossil | 1970.076 | 2.313 | 0.808 | 10230.4343 | [7 empty] | RFC Michigan | RFC Michigan
Heating Oil (No. 2) CO2 Emission Factor | 22300 | lb/103 gal | U.S. Environmental Protection Agency, AP 42, Fifth Edition, Volume I. Chapter 1: External Combustion Sources, Section 3. Fuel Oil Combustion, Background Document. Table 6. |  |  | http://www.epa.gov/ttn/chief/ap42/ch01/bgdocs/b01s03.pdf |  |  |  | 67 | RFC East | 98917.2 | 1438967008.865 | 283222517.682 | 83501.751 | 80873.252 | 107366532.11 | 0.59 | 0.571 | 758.178 | 0.116 | 0.101 | 0.112 | 149.227 | 0.877 | 0.972 | 1328.802 | 0.102 | 0.113 | 154.195 | 49897428.132 | 704722.297 | 107690209.774 | 595561.112 | 17.6177 | 0.24882 | 38.0232 | 0.21028 | 58.0094 | 5080.6942 | 8758.3981 | [19 empty] | IN_Fossil | 1965.829 | 1.887 | 1.762 | 9929.5802 | [7 empty] | RFC West | RFC West
Heating Oil (No. 2) SO2 Emission Factor | 142 | lb/103 gal | U.S. Environmental Protection Agency, AP 42, Fifth Edition, Volume I. Chapter 1: External Combustion Sources, Section 3. Fuel Oil Combustion, Final Document. Table 1.3-1 |  |  | http://www.epa.gov/ttn/chief/ap42/ch01/bgdocs/b01s03.pdf |  |  |  | 68 | RFC Michigan | 32930.2 | 682504960.262 | 92326063.429 | 41784.303 | 78957.993 | 58721433.775 | 0.905 | 1.71 | 1272.045 | 0.122 | 0.115 | 0.231 | 172.076 | 1.017 | 2.223 | 1670.193 | 0.108 | 0.236 | 177.582 | 38380195.509 | 807100.326 | 29084085.977 | 1744791.617 | 41.4836 | 0.87236 | 31.4358 | 1.8859 | 77.6841 | 7392.3325 | 9496.0495 | [19 empty] | KS_Fossil | 2262.592 | 0.568 | 1.401 | 11156.2812 | [7 empty] | WECC Rockies | WECC Rockies
Heating Oil (No. 2) NOX Emission Factor | 24 | lb/103 gal | U.S. Environmental Protection Agency, AP 42, Fifth Edition, Volume I. Chapter 1: External Combustion Sources, Section 3. Fuel Oil Combustion, Background Document. Table 2. |  |  | http://www.epa.gov/ttn/chief/ap42/ch01/bgdocs/b01s03.pdf |  |  |  | 69 | RFC West | 185858.1 | 3532707666.443 | 533500666.079 | 252108.059 | 319788.204 | 331687820.704 | 0.945 | 1.199 | 1243.439 | 0.143 | 0.135 | 0.181 | 187.781 | 1.33 | 1.774 | 1851.15 | 0.136 | 0.182 | 189.541 | 265673932.741 | 2047709.608 | 89082052.013 | 3690216.235 | 49.7645 | 0.38356 | 16.6863 | 0.69123 | 68.229 | 6621.7493 | 9698.6032 | [19 empty] | KY_Fossil | 2055.81 | 1.992 | 1.507 | 10349.9523 | [7 empty] | SPP North | SPP North
U.S. Transmission and Distribution Electricity Losses | 5% | Percent | U.S. Energy Information Administration, Frequently Asked Questions, "How much electricity is lost in transmission and distribution in the United States?" |  |  | http://www.eia.gov/tools/faqs/faq.cfm?id=105&t=3 |  |  |  | 70 | WECC Rockies | 23338.6 | 465518924.814 | 63912176.716 | 32455.043 | 20372.964 | 43708529.791 | 1.016 | 0.638 | 1367.768 | 0.139 | 0.135 | 0.088 | 187.784 | 1.395 | 0.889 | 1910.566 | 0.138 | 0.088 | 188.59 | 32809028.617 | 6881.544 | 12938619.522 | 0 | 51.3346 | 0.010767 | 20.2444 | 0 | 71.9272 | 7283.7282 | 10126.5319 | [19 empty] | LA_Fossil | 1113.707 | 0.871 | 1.029 | 7700.1004 | [7 empty] | SPP South | SPP South
Metric Tons of CO2e per passenger vehicle per year | 4.73 | tonnes | U.S. Environmental Protection Agency, Greenhouse Gas Equivalencies Calculator, Calculations and References, Passenger Vehicles per Year |  |  | https://www.epa.gov/energy/ghg-equivalencies-calculator-calculations-and-references |  |  |  | 71 | SPP North | 28325.7 | 473914984.366 | 66741590.205 | 26760.077 | 15319.266 | 47131234.183 | 0.802 | 0.459 | 1412.35 | 0.113 | 0.117 | 0.065 | 198.902 | 1.162 | 0.68 | 2094.389 | 0.111 | 0.065 | 199.308 | 38618864.747 | 62175.706 | 6313925.846 | 8979.192 | 57.8633 | 0.093159 | 9.4603 | 0.013454 | 67.5567 | 7100.7446 | 10510.7977 | [19 empty] | MA_Fossil | 989.178 | 0.154 | 0.283 | 8420.1664 | [7 empty] | SERC Mississippi Valley | SERC Mississippi Valley
Metric Tons of CO2 per home electricity usage per year | 6.772 | tonnes | U.S. Environmental Protection Agency, Greenhouse Gas Equivalencies Calculator, Calculations and References, Home Electricity Use |  |  | https://www.epa.gov/energy/ghg-equivalencies-calculator-calculations-and-references |  |  |  | 72 | SPP South | 61022.2 | 1168681128.398 | 156780736.6 | 66645.294 | 130141.537 | 97856946.56 | 0.85 | 1.66 | 1248.329 | 0.114 | 0.114 | 0.223 | 167.466 | 1.075 | 2.096 | 1605.406 | 0.113 | 0.221 | 169.144 | 54597493.328 | 3003411.733 | 63740760.922 | 362372.682 | 34.8241 | 1.9157 | 40.656 | 0.23113 | 79.153 | 7454.2393 | 9417.5099 | [19 empty] | MD_Fossil | 1901.952 | 1.707 | 0.982 | 10526.6401 | [7 empty] | SERC Midwest | SERC Midwest
U.S. Emissions Data (CO2, SO2, NOX) | --- | --- | eGRID2018 Version 1.0, 2016 Data |  |  | https://www.epa.gov/energy/emissions-generation-resource-integrated-database-egrid |  |  |  | 73 | SERC Mississippi Valley | 58822.1 | 1045376394.06 | 172359088.287 | 68917.791 | 61393.879 | 72295070.886 | 0.8 | 0.712 | 838.889 | 0.132 | 0.142 | 0.117 | 138.314 | 1.059 | 0.913 | 1125.776 | 0.133 | 0.115 | 141.585 | 24129336.7 | 1896629.072 | 101157013.093 | 2480343.744 | 13.9995 | 1.1004 | 58.6897 | 1.4391 | 77.4014 | 6065.1075 | 7835.914 | [19 empty] | ME_Fossil | 850.006 | 0.208 | 0.181 | 8554.1044 | [7 empty] | SERC South | SERC South
Canada Emissions Data (CO2) | --- | --- | National Inventory Report, Greenhouse Gas Sources and Sinks in Canada 1990-2011, Environment Canada, Part 3. |  |  | http://www.ec.gc.ca/ges-ghg/ |  |  |  | 74 | SERC Midwest | 38431.8 | 970603254.45 | 121294300.829 | 68820.981 | 147901.443 | 97799013.798 | 1.135 | 2.439 | 1612.59 | 0.142 | 0.135 | 0.305 | 201.522 | 1.403 | 3.036 | 2017.466 | 0.14 | 0.304 | 201.869 | 86572611.521 | 96460.948 | 10058051.501 | 2927.009 | 71.374 | 0.079526 | 8.2923 | 0.0024131 | 80.1269 | 8002.0516 | 9986.7248 | [19 empty] | MI_Fossil | 1699.032 | 2.329 | 1.104 | 9547.2589 | [7 empty] | SERC Tennessee Valley | SERC Tennessee Valley
Canada Emissions Data (SO2, NOX) | --- | --- | National Pollutant Release Inventory (NPRI) Downloadable Datasets, 2011 Air Pollutant Emission Summaries and Trends. 2011 Emissions from Electric Power Generation (Utilities) |  |  | http://www.ec.gc.ca/inrp-npri/default.asp?lang=en&n=0EC58C98-#Emission_Summaries |  |  |  | 75 | SERC South | 87369.9 | 1840654945.935 | 264562048.583 | 67449.06 | 49118.205 | 144103497.26 | 0.51 | 0.371 | 1089.374 | 0.073 | 0.061 | 0.053 | 156.579 | 0.607 | 0.394 | 1424.911 | 0.069 | 0.045 | 161.278 | 76495154.618 | 272745.89 | 124394375.036 | 126318.162 | 28.9139 | 0.10309 | 47.019 | 0.047746 | 79.5414 | 6957.3658 | 8746.8451 | [19 empty] | MN_Fossil | 1853.687 | 0.987 | 1.033 | 9895.2484 | [7 empty] | SERC Virginia/Carolina | SERC Virginia/Carolina
[10 empty] | 76 | SERC Tennessee Valley | 73445.6 | 1450138431.237 | 222211053.325 | 79876.949 | 111496.645 | 131708173.544 | 0.719 | 1.004 | 1185.433 | 0.11 | 0.105 | 0.154 | 181.649 | 1.03 | 1.46 | 1747.319 | 0.108 | 0.153 | 182.835 | 97090495.699 | 1339531.911 | 51931731.032 | 68864.956 | 43.6929 | 0.60282 | 23.3705 | 0.030991 | 68.465 | 6525.9509 | 9531.8061 | [19 empty] | MO_Fossil | 1998.954 | 2.992 | 1.707 | 9833.0348 | [7 empty] | Alaska Systems Coordinating Council | Alaska Systems Coordinating Council
Calculations | [9 empty] | 77 | SERC Virginia/Carolina | 113211.4 | 1672349131.41 | 324246073.998 | 77512.327 | 55479.991 | 130555267.593 | 0.478 | 0.342 | 805.285 | 0.093 | 0.089 | 0.066 | 156.134 | 0.72 | 0.523 | 1444.139 | 0.081 | 0.059 | 162.899 | 80637825.476 | 802191.301 | 95625623.256 | 408359.055 | 24.8693 | 0.2474 | 29.4917 | 0.12594 | 57.6603 | 5157.6542 | 8944.8925 | [19 empty] | MS_Fossil | 1060.249 | 0.129 | 0.474 | 8009.769 | [7 empty] | Florida Reliability Coordinating Council | Florida Reliability Coordinating Council
[10 empty] | 78 | Alaska Systems Coordinating Council | 3379.6 | 42502215.628 | 6232862.512 | 20923.634 | 1741.089 | 2928528.764 | 6.714 | 0.559 | 939.706 | 0.985 | 0.961 | 0.082 | 137.806 | 9.238 | 0.775 | 1310.998 | 0.98 | 0.082 | 139.116 | 594138.933 | 826059.647 | 3040487.303 | 0 | 9.5287 | 13.2482 | 48.7628 | 0 | 72.1913 | 6819.0523 | 9442.187 | [19 empty] | MT_Fossil | 2284.625 | 1.866 | 2.049 | 10796.4426 | [7 empty] | Hawaiian Islands Coordinating Council | Hawaiian Islands Coordinating Council
Description | Value | Units | [7 empty] | 79 | Florida Reliability Coordinating Council | 97820.3 | 1665956580.815 | 229407929.06 | 61022.225 | 42714.18 | 116043999.116 | 0.532 | 0.372 | 1011.683 | 0.073 | 0.073 | 0.051 | 139.312 | 0.529 | 0.425 | 1183.524 | 0.064 | 0.052 | 143.661 | 36790857.618 | 2814817.331 | 152730470.895 | 19074.17 | 16.0373 | 1.227 | 66.5759 | 0.0083145 | 87.0268 | 7261.9834 | 8344.5409 | [19 empty] | NC_Fossil | 1462.692 | 0.61 | 0.836 | 8787.8422 | [7 empty] | Midwest Reliability Organization | Midwest Reliability Organization
User Input | US Average | [8 empty] | 80 | Hawaiian Islands Coordinating Council | 3222 | 92598221.117 | 9948844.667 | 22344.851 | 37331.598 | 7571577.478 | 4.492 | 7.505 | 1522.102 | 0.483 | 0.461 | 0.806 | 163.536 | 5.084 | 8.905 | 1721.957 | 0.509 | 0.891 | 172.262 | 1497379.514 | 6640316.096 | 0 | 63380.048 | 15.0508 | 66.7446 | 0 | 0.63706 | 89.1587 | 9307.4346 | 10439.1823 | [19 empty] | ND_Fossil | 2271.526 | 3.268 | 2.703 | 10616.2779 | [7 empty] | No NERC region | No NERC region
User Input | US Average Fossil | [8 empty] | 81 | Midwest Reliability Organization | 82125.5 | 1388890444.248 | 222684937.84 | 114754.832 | 158524.388 | 135918531.637 | 1.031 | 1.424 | 1220.725 | 0.165 | 0.156 | 0.228 | 195.722 | 1.586 | 2.33 | 2021.001 | 0.158 | 0.232 | 200.861 | 114629707.608 | 473530.838 | 18765614.811 | 82668.27 | 51.4762 | 0.21265 | 8.427 | 0.037123 | 62.1377 | 6237.0201 | 10037.4193 | [19 empty] | NE_Fossil | 2122.981 | 4.591 | 1.8 | 10257.1058 | [7 empty] | Northeast Power Coordinating Council | Northeast Power Coordinating Council
Electricity Consumption (kWh/yr) | 8631578.9474 | kWh | 0 | 0 |  | 0 | 0 | 0 | 0 | 82 | No NERC region | 313.5 | 50865 | 102170.999 | 84.501 | 7.376 | 4153.78 | 1.654 | 0.144 | 81.31 | 3.323 | 3.323 | 0.29 | 163.326 | 32.069 | 2.799 | 1576.387 | 3.323 | 0.29 | 163.326 | 0 | 5270 | 0 | 0 | 0 | 5.158 | 0 | 0 | 5.158 | 497.8419 | 9651.8027 | [19 empty] | NH_Fossil | 965.006 | 0.121 | 0.315 | 9813.8459 | [7 empty] | Reliability First Corporation | Reliability First Corporation
Natural Gas Consumption (MMBtu/yr) | 0 | MMBtu | 36086.4771 | 57048.5329 |  | 55890.2656 | 33210 | 0 | 0 | 83 | Northeast Power Coordinating Council | 97261.4 | 1085984479.693 | 241854386.093 | 44058.224 | 15936.911 | 61176490.518 | 0.364 | 0.132 | 505.895 | 0.081 | 0.076 | 0.029 | 112.665 | 0.363 | 0.202 | 967.841 | 0.046 | 0.026 | 123.435 | 4314380.178 | 1332385.058 | 110094164.068 | 149107.778 | 1.7839 | 0.5509 | 45.5208 | 0.061652 | 52.9117 | 4490.241 | 8486.2978 | [19 empty] | NJ_Fossil | 914.086 | 0.059 | 0.227 | 7675.5548 | [7 empty] | SERC Reliability Corporation | SERC Reliability Corporation
Annual Propane Consumption (gal) | 0 | gal | 0 | 0 |  | 0 | 0 | 0 | 0 | 84 | Reliability First Corporation | 322697.4 | 5794829249.229 | 923709999.195 | 381083.167 | 482630.819 | 510088974.228 | 0.825 | 1.045 | 1104.435 | 0.132 | 0.122 | 0.167 | 176.05 | 1.153 | 1.582 | 1687.887 | 0.123 | 0.168 | 179.485 | 363193124.575 | 3597455.556 | 231761882.088 | 6028251.298 | 39.3036 | 0.3893 | 25.0805 | 0.65236 | 66.6298 | 6273.4292 | 9411.6597 | [19 empty] | NM_Fossil | 1823.793 | 0.582 | 2.728 | 10080.4263 | [7 empty] | Southwest Power Pool | Southwest Power Pool
Annual Heating Oil Consumption (gal) | 0 | gal | 0 | 0 |  | 0 | 0 | 0 | 0 | 85 | SERC Reliability Corporation | 368670.4 | 6884052706.637 | 1095680923.107 | 358316.238 | 421711.107 | 567033244.656 | 0.654 | 0.77 | 1035.034 | 0.104 | 0.099 | 0.123 | 164.738 | 0.895 | 1.067 | 1511.17 | 0.1 | 0.119 | 168.579 | 355914523.914 | 4389257.38 | 384078635.403 | 3078868.075 | 32.4834 | 0.4006 | 35.0539 | 0.281 | 70.4286 | 6282.8991 | 8920.9522 | [19 empty] | NV_Fossil | 962.473 | 0.174 | 0.586 | 7556.2698 | [7 empty] | Texas Regional Entity | Texas Regional Entity
[10 empty] | 86 | Southwest Power Pool | 93253.7 | 1684653506.963 | 232265414.718 | 94859.113 | 145736.677 | 147592118.164 | 0.817 | 1.255 | 1270.892 | 0.113 | 0.113 | 0.173 | 175.22 | 1.085 | 1.662 | 1714.398 | 0.112 | 0.171 | 176.543 | 93506291.305 | 3066775.722 | 75032292.134 | 379296.725 | 40.2584 | 1.3204 | 32.3045 | 0.1633 | 75.2021 | 7253.1397 | 9644.8617 | [19 empty] | NY_Fossil | 1000.197 | 0.295 | 0.446 | 8519.0145 | [7 empty] | Western Electricity Coordinating Council | Western Electricity Coordinating Council
[10 empty] | 87 | Texas Regional Entity | 156270.6 | 2411729656.672 | 382787774.959 | 105372.072 | 201819.144 | 194209916.009 | 0.551 | 1.054 | 1014.713 | 0.087 | 0.086 | 0.167 | 161.054 | 0.708 | 1.41 | 1360.705 | 0.084 | 0.168 | 161.852 | 101006612.69 | 178137.041 | 182135317.435 | 1838398.994 | 26.3871 | 0.046537 | 47.5813 | 0.48027 | 74.9501 | 6300.4354 | 8406.1753 | [19 empty] | OH_Fossil | 1753.902 | 2.131 | 1.116 | 9476.4302 | [7 empty] | Canada Average | Canada Average
State Abbrev | US Average | --- | [7 empty] | 88 | Western Electricity Coordinating Council | 289992.4 | 3630195388.817 | 730647397.939 | 266227.722 | 118076.829 | 291921795.465 | 0.729 | 0.323 | 799.077 | 0.147 | 0.141 | 0.065 | 160.83 | 1.243 | 0.575 | 1485.001 | 0.138 | 0.064 | 165.288 | 167701636.785 | 870835.706 | 219817457.546 | 2250023.521 | 22.9525 | 0.11919 | 30.0853 | 0.30795 | 55 | 4968.4641 | 9033.5662 | [19 empty] | OK_Fossil | 1474.508 | 1.789 | 0.969 | 9335.3296 | [7 empty] | Alberta | Alberta
U.S. State Selected? | Yes | Y/N | [58 empty] | OR_Fossil | 1062.003 | 0.437 | 0.85 | 8393.0521 | [7 empty] | British Columbia | British Columbia
U.S. Fossil Emissions Profile? | Yes | Y/N | [58 empty] | PA_Fossil | 1467.227 | 1.613 | 1.291 | 8956.8414 | [7 empty] | Manitoba | Manitoba
Heat Rate | 8715.3973 | Btu/kWh | [58 empty] | RI_Fossil | 905.025 | 0.013 | 0.214 | 7669.1646 | [7 empty] | New Brunswick | New Brunswick
Electricity CO2 Emission Rate | 1565.2376 | lb/MWh | [58 empty] | SC_Fossil | 1589.85 | 0.52 | 0.618 | 9329.0243 | [7 empty] | Newfoundland | Newfoundland
Electricity SO2 Emission Rate | 1.2484 | lb/MWh | [58 empty] | SD_Fossil | 1758.21 | 0.486 | 0.707 | 9557.1337 | [7 empty] | Nova Scotia | Nova Scotia
Electricity NOX Emission Rate | 1.4468 | lb/MWh | [58 empty] | TN_Fossil | 1831.783 | 1.454 | 0.913 | 9670.2766 | [7 empty] | Ontario | Ontario
Natural Gas CO2 Emission Rate | 117.6471 | lb/MMBtu | [58 empty] | TX_Fossil | 1360.568 | 1.406 | 0.757 | 8474.4186 | [7 empty] | Prince Edward Island | Prince Edward Island
Natural Gas SO2 Emission Rate | 0.00058824 | lb/MMBtu | [58 empty] | UT_Fossil | 1777.411 | 0.952 | 1.897 | 9460.7895 | [7 empty] | Quebec | Quebec
Natural Gas NOX Emission Rate | 0.12342 | lb/MMBtu | [58 empty] | VA_Fossil | 1243.007 | 0.353 | 0.634 | 8750.3102 | [7 empty] | Saskatchewan | Saskatchewan
Propane CO2 Emission Rate | 12500 | lb/103 gal | [58 empty] | VT_Fossil | 3251.2 | 4.122 | 8.495 | 10379.7318
Propane SO2 Emission Rate | 0.1 | lb/103 gal | [58 empty] | WA_Fossil | 1319.577 | 0.187 | 0.815 | 8552.9028
Propane NOX Emission Rate | 13 | lb/103 gal | [58 empty] | WI_Fossil | 1838.705 | 0.627 | 0.688 | 9791.2296
Heating Oil CO2 Emission Rate | 22300 | lb/103 gal | [58 empty] | WV_Fossil | 2058.656 | 1.23 | 1.386 | 10049.9428
Heating Oil SO2 Emission Rate | 142 | lb/103 gal | [58 empty] | WY_Fossil | 2324.747 | 1.609 | 1.823 | 11003.1178
Heating Oil NOX Emission Rate | 24 | lb/103 gal | [58 empty] | ASCC Alaska Grid | 1072.28 | 0.828 | 0.832 | 7870.8544
Electricity Consumption | 75227.6396 | MMBtu | 0 | 0 |  | 0 | 0 | 0 | 0 | [51 empty] | ASCC Miscellaneous | 503.125 | 2.055 | 1.938 | 3386.0007
Electricity CO2 Emissions | 13510472.1527 | lb | 0 | 0 |  | 0 | 0 | 0 | 0 | [51 empty] | WECC Southwest | 1043.645 | 0.151 | 0.138 | 6373.8653
Electricity SO2 Emissions | 10775.4262 | lb | 0 | 0 |  | 0 | 0 | 0 | 0 | [51 empty] | WECC California | 527.862 | 0.129 | 0.125 | 4408.7126
Electricity NOX Emissions | 12488.2023 | lb | 0 | 0 |  | 0 | 0 | 0 | 0 | [51 empty] | ERCOT All | 1009.156 | 0.087 | 0.085 | 6294.7048
Annual Natural Gas Consumption (MMBtu) | 0 | MMBtu | 36086.4771 | 57048.5329 |  | 55890.2656 | 33210 | 0 | 0 | [51 empty] | FRCC All | 1011.683 | 0.073 | 0.073 | 7261.9834
Natural Gas CO2 Emissions | 0 | lb | 4245467.8933 | 6711592.1053 |  | 6575325.3632 | 3907058.8235 | 0 | 0 | [51 empty] | HICC Miscellaneous | 1152.016 | 1.015 | 0.996 | 7335.8317
Natural Gas SO2 Emissions | 0 | lb | 21.2273 | 33.558 |  | 32.8766 | 19.5353 | 0 | 0 | [51 empty] | HICC Oahu | 1662.888 | 0.335 | 0.319 | 10057.4617
Natural Gas NOX Emissions | 0 | lb | 4453.8103 | 7040.9573 |  | 6898.0034 | 4098.7941 | 0 | 0 | [51 empty] | MRO East | 1668.212 | 0.116 | 0.114 | 9056.3674
Propane Consumption | 0 | MMBtu | 0 | 0 |  | 0 | 0 | 0 | 0 | [51 empty] | MRO West | 1238.817 | 0.168 | 0.159 | 6227.0867
Propane CO2 Emissions | 0 | lb | 0 | 0 |  | 0 | 0 | 0 | 0 | [51 empty] | NPCC New England | 558.156 | 0.075 | 0.067 | 5175.8403
Propane SO2 Emissions | 0 | lb | 0 | 0 |  | 0 | 0 | 0 | 0 | [51 empty] | WECC Northwest | 651.199 | 0.163 | 0.162 | 3756.8498
Propane NOX Emissions | 0 | lb | 0 | 0 |  | 0 | 0 | 0 | 0 | [51 empty] | NPCC NYC/Westchester | 635.81 | 0.048 | 0.054 | 5363.5995
Heating Oil Consumption | 0 | MMBtu | 0 | 0 |  | 0 | 0 | 0 | 0 | [51 empty] | NPCC Long Island | 1178.322 | 0.086 | 0.081 | 10055.2303
Heating Oil CO2 Emissions | 0 | lb | 0 | 0 |  | 0 | 0 | 0 | 0 | [51 empty] | NPCC Upstate NY | 294.661 | 0.117 | 0.109 | 2509.38
Heating Oil SO2 Emissions | 0 | lb | 0 | 0 |  | 0 | 0 | 0 | 0 | [51 empty] | RFC East | 758.178 | 0.116 | 0.101 | 5080.6942
Heating Oil NOX Emissions | 0 | lb | 0 | 0 |  | 0 | 0 | 0 | 0 | [51 empty] | RFC Michigan | 1272.045 | 0.122 | 0.115 | 7392.3325
Total CO2 Emissions | 13510472.1527 | lb | 4245467.8933 | 6711592.1053 |  | 6575325.3632 | 3907058.8235 | 0 | 0 | [51 empty] | RFC West | 1243.439 | 0.143 | 0.135 | 6621.7493
Total SO2 Emissions | 10775.4262 | lb | 21.2273 | 33.558 |  | 32.8766 | 19.5353 | 0 | 0 | [51 empty] | WECC Rockies | 1367.768 | 0.139 | 0.135 | 7283.7282
Total NOX Emissions | 12488.2023 | lb | 4453.8103 | 7040.9573 |  | 6898.0034 | 4098.7941 | 0 | 0 | [51 empty] | SPP North | 1412.35 | 0.113 | 0.117 | 7100.7446
CO2 Emission Savings | 0 | lb | 9265004.2594 | 6798880.0475 |  | 6935146.7895 | 9603413.3292 | 13510472.1527 | 13510472.1527 | [51 empty] | SPP South | 1248.329 | 0.114 | 0.114 | 7454.2393
SO2 Emission Savings | 0 | lb | 10754.1989 | 10741.8683 |  | 10742.5496 | 10755.8909 | 10775.4262 | 10775.4262 | [51 empty] | SERC Mississippi Valley | 838.889 | 0.132 | 0.142 | 6065.1075
NOX Emission Savings | 0 | lb | 8034.392 | 5447.245 |  | 5590.1989 | 8389.4082 | 12488.2023 | 12488.2023 | [51 empty] | SERC Midwest | 1612.59 | 0.142 | 0.135 | 8002.0516
CO2 Emissions Delta | 0 | metric tons | 4202.5784 | 3083.9518 |  | 3145.7619 | 4356.0797 | 6128.31 | 6128.31 | [51 empty] | SERC South | 1089.374 | 0.073 | 0.061 | 6957.3658
Cars off Highway (CO2 Equivalent) | 0 | cars | 888.4944 | 651.9983 |  | 665.066 | 920.9471 | 1295.6258 | 1295.6258 | [51 empty] | SERC Tennessee Valley | 1185.433 | 0.11 | 0.105 | 6525.9509
Home Electricity Usage (CO2 Equivalent) | 0 | homes | 620.5816 | 455.3975 |  | 464.5248 | 643.2486 | 904.9483 | 904.9483 | [51 empty] | SERC Virginia/Carolina | 805.285 | 0.093 | 0.089 | 5157.6542
[61 empty] | Alaska Systems Coordinating Council | 939.706 | 0.985 | 0.961 | 6819.0523
[61 empty] | Florida Reliability Coordinating Council | 1011.683 | 0.073 | 0.073 | 7261.9834
[61 empty] | Hawaiian Islands Coordinating Council | 1522.102 | 0.483 | 0.461 | 9307.4346
[61 empty] | Midwest Reliability Organization | 1220.725 | 0.165 | 0.156 | 6237.0201
[61 empty] | No NERC region | 81.31 | 3.323 | 3.323 | 497.8419
[61 empty] | Northeast Power Coordinating Council | 505.895 | 0.081 | 0.076 | 4490.241
[61 empty] | Reliability First Corporation | 1104.435 | 0.132 | 0.122 | 6273.4292
[61 empty] | SERC Reliability Corporation | 1035.034 | 0.104 | 0.099 | 6282.8991
[61 empty] | Southwest Power Pool | 1270.892 | 0.113 | 0.113 | 7253.1397
[61 empty] | Texas Regional Entity | 1014.713 | 0.087 | 0.086 | 6300.4354
[61 empty] | Western Electricity Coordinating Council | 799.077 | 0.147 | 0.141 | 4968.4641
[61 empty] | ASCC Alaska Grid_Fossil | 1281.606 | 0.624 | 7.658 | 9312.4659
[61 empty] | ASCC Miscellaneous_Fossil | 1530.678 | 1.913 | 21.126 | 10418.2578
[61 empty] | WECC Southwest_Fossil | 1497 | 0.371 | 1.364 | 9130.7935
[61 empty] | WECC California_Fossil | 956.99 | 0.061 | 0.79 | 7783.1875
[61 empty] | ERCOT All_Fossil | 1351.141 | 1.382 | 0.699 | 8386.2622
[61 empty] | FRCC All_Fossil | 1183.524 | 0.425 | 0.529 | 8344.5409
[61 empty] | HICC Miscellaneous_Fossil | 1688.235 | 6.588 | 10.913 | 10440.2001
[61 empty] | HICC Oahu_Fossil | 1731.629 | 9.57 | 3.412 | 10438.9
[61 empty] | MRO East_Fossil | 1969.779 | 1.392 | 0.98 | 9930.3177
[61 empty] | MRO West_Fossil | 2068.415 | 2.311 | 1.654 | 10192.2042
[61 empty] | NPCC New England_Fossil | 933.923 | 0.104 | 0.267 | 8454.2103
[61 empty] | WECC Northwest_Fossil | 1706.11 | 1.112 | 1.468 | 9468.5309
[61 empty] | NPCC NYC/Westchester_Fossil | 952.759 | 0.016 | 0.324 | 8133.8586
[61 empty] | NPCC Long Island_Fossil | 1129.489 | 0.16 | 0.632 | 10136.7258
[61 empty] | NPCC Upstate NY_Fossil | 947.055 | 0.601 | 0.424 | 7798.3463
[61 empty] | RFC East_Fossil | 1328.802 | 0.972 | 0.877 | 8758.3981
[61 empty] | RFC Michigan_Fossil | 1670.193 | 2.223 | 1.017 | 9496.0495
[61 empty] | RFC West_Fossil | 1851.15 | 1.774 | 1.33 | 9698.6032
[61 empty] | WECC Rockies_Fossil | 1910.566 | 0.889 | 1.395 | 10126.5319
[61 empty] | SPP North_Fossil | 2094.389 | 0.68 | 1.162 | 10510.7977
[61 empty] | SPP South_Fossil | 1605.406 | 2.096 | 1.075 | 9417.5099
[61 empty] | SERC Mississippi Valley_Fossil | 1125.776 | 0.913 | 1.059 | 7835.914
[61 empty] | SERC Midwest_Fossil | 2017.466 | 3.036 | 1.403 | 9986.7248
[61 empty] | SERC South_Fossil | 1424.911 | 0.394 | 0.607 | 8746.8451
|  | Map of NERC Regions | [58 empty] | SERC Tennessee Valley_Fossil | 1747.319 | 1.46 | 1.03 | 9531.8061
[61 empty] | SERC Virginia/Carolina_Fossil | 1444.139 | 0.523 | 0.72 | 8944.8925
[61 empty] | Alaska Systems Coordinating Council_Fossil | 1310.998 | 0.775 | 9.238 | 9442.187
[61 empty] | Florida Reliability Coordinating Council_Fossil | 1183.524 | 0.425 | 0.529 | 8344.5409
[61 empty] | Hawaiian Islands Coordinating Council_Fossil | 1721.957 | 8.905 | 5.084 | 10439.1823
[61 empty] | Midwest Reliability Organization_Fossil | 2021.001 | 2.33 | 1.586 | 10037.4193
[61 empty] | No NERC region_Fossil | 1576.387 | 2.799 | 32.069 | 9651.8027
[61 empty] | Northeast Power Coordinating Council_Fossil | 967.841 | 0.202 | 0.363 | 8486.2978
[61 empty] | Reliability First Corporation_Fossil | 1687.887 | 1.582 | 1.153 | 9411.6597
[61 empty] | SERC Reliability Corporation_Fossil | 1511.17 | 1.067 | 0.895 | 8920.9522
[61 empty] | Southwest Power Pool_Fossil | 1714.398 | 1.662 | 1.085 | 9644.8617
[61 empty] | Texas Regional Entity_Fossil | 1360.705 | 1.41 | 0.708 | 8406.1753
[61 empty] | Western Electricity Coordinating Council_Fossil | 1485.001 | 0.575 | 1.243 | 9033.5662
[61 empty] | Canada Average | 361.5584 | 1.1415 | 0.71692 | 3634
[61 empty] | Alberta | 1410.56 | 3.9073 | 2.8677 | 12388
[61 empty] | British Columbia | 24.9123 | 0.0054315 | 0.081796 | 437
[61 empty] | Manitoba | 7.3194 | 0.041752 | 0.027767 | 300
[61 empty] | New Brunswick | 1237 | 0.95782 | 1.3789 | 7582
[61 empty] | Newfoundland | 44.9743 | 0.16351 | 0.17453 | 365
[61 empty] | Nova Scotia | 1582.9 | 12.5771 | 3.5649 | 7980
[61 empty] | Ontario | 876 | 0.17477 | 0.27723 | 7582
[61 empty] | Prince Edward Island | 4.2329 | 0.29408 | 0.12027 | 7864
[61 empty] | Quebec | 4.4092 | 0.020215 | 0.10307 | 101
[61 empty] | Saskatchewan | 1642.4452 | 9.7426 | 3.9009 | 5711
[62 empty] | CO2 Emission Rate (lb/MWh) | SO2 Emission Rate (lb/MWh) | NOX Emission Rate (lb/MWh) | Annual Heat Rate (Btu/kWh)
**Ontario #'s replaced to include Marginal Power Mix as provided by Enbridge Gas on 8/14/16, then updated NB and NS per Enbridge on 9/13/16
[61 empty] | Orig Ontario All source | 216.1 |  |  | 2686
[61 empty] | Orig New Brunswick | 976.6 |  |  | 2720
[61 empty] | Nova Scotia | 1582.9 (no change) |  |  | Changed
[61 empty] | Alberta | 1629.2 |  |  | 10177
[61 empty] | Orig formulas >>>> (alberta example) | 0 | 0 | 0 | 0
…for other provinces
** update cels F25 and E26 for notes on marginal mix
Disclaimer: This calculator was prepared for work sponsored by the Energy Solutions Center Inc. Neither The Energy Solutions Center, any member of The Energy Solutions Center, nor any person on behalf of any or all of them:
a) Makes any warranty or representation, express or implied, with respect to the accuracy, completeness, or usefulness of the information contained in this application or report, or
b) Assumes any liability with respect to the use of or for damages resulting from the use of any information disclosed in this application or report.
Notes:
1) For U.S. states, eGrid subregions, and NERC regions, select one of two eGRID U.S. emission profile options - 'Average All Sources' or Average Fossil'.
2) For Canadian provinces, please select the Canadian emissions profile option.
3) To view eGrid subregion and NERC region maps, click here.
Note: A negative value represents an increase in emissions.
Note: Annual Electricity Consumption includes losses from Transmission & Distribution.

## _SSC (hidden)
_Ctrl_1 | {"WidgetClassification":0,"State":1,"IsRequired":true,"IsMultiline":false,"IsHidden":false,"Placeholder":"","InputType":0,"Rows":3,"IsMergeJustify":false,"CellName":"_Ctrl_1","CellAddress":"='CHP Payback'!$B$6","WidgetName":4,"HiddenRow":1,"SheetCodeName":null,"ControlId":"Company Name"} | {"IsHide":false,"SheetId":1,"Name":"CHP Payback","HiddenRow":1,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}} | {"ButtonStyle":0,"Name":"","HideSscPoweredlogo":false,"CopyProtect":{"IsEnabled":false,"DomainName":""},"Theme":{"BgColor":"#FFFFFFFF","BgImage":"","InputBorderStyle":2},"Layout":0,"SmartphoneSettings":{"ViewportLock":true,"UseOldViewEngine":false,"EnableZoom":false,"EnableSwipe":false,"HideToolbar":false,"CheckboxFlavor":1},"SmartphoneTheme":0,"InputDetection":0,"Toolbar":{"Position":1,"IsSubmit":true,"IsPrint":true,"IsPrintAll":false,"IsReset":true,"IsUpdate":true},"AspnetConfig":{"BrowseUrl":"http://localhost/ssc","FileExtension":0},"ConfigureSubmit":{"IsShowCaptcha":false,"IsUseSscWebServer":true,"ReceiverCode":"","IsFreeService":false,"IsAdvanceService":false,"IsDemonstrationService":true,"AfterSuccessfulSubmit":"","AfterFailSubmit":"","AfterCancelWizard":"","IsUseOwnWebServer":false,"OwnWebServerURL":"","OwnWebServerTarget":"","SubmitTarget":0},"Flavor":0,"Edition":3,"IgnoreBgInputCell":false} | {"Captcha":{"Heading":"Enter the number displayed below.","Message":"This is to verify that you are a human visitor, to prevent automated form submissions.","OkButton":"OK","CancelButton":"Cancel","ErrorMessage":"Your answer is incorrect, please try again."},"RequiredField":{"ErrorMessage":"The fields with the red border are required.","OkButton":"OK","DDLDefaultRequiredText":"Please Select"},"WizardButton":{"Next":"Next","Previous":"Previous","Cancel":"Cancel","Finish":"Finish"},"ToolbarButton":{"Submit":"Submit","Print":"Print","PrintAll":"Print All","Reset":"Reset","Update":"Update","Back":"Back"},"BrowserAndLocation":{"Browsers":[],"ConversionPath":"C:\\Users\\Owner\\Documents\\SpreadsheetConverter"},"AdvancedSettingsModels":[],"Dropbox":{"AccessToken":"","AccessSecret":""},"SpreadsheetServer":{"Username":"","Password":"","ServerUrl":""},"ConfigureSubmitDefault":{"Email":""}}
_Ctrl_2 | {"WidgetClassification":0,"State":1,"IsRequired":true,"IsMultiline":false,"IsHidden":false,"Placeholder":"","InputType":0,"Rows":3,"IsMergeJustify":false,"CellName":"_Ctrl_2","CellAddress":"='CHP Payback'!$D$6","WidgetName":4,"HiddenRow":2,"SheetCodeName":null,"ControlId":"Location"} | {"IsHide":true,"SheetId":2,"Name":"Overview","HiddenRow":2,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}}
{"IsHide":true,"SheetId":3,"Name":"Assumptions","HiddenRow":3,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}}
{"IsHide":true,"SheetId":4,"Name":"Life Cycle Cost ","HiddenRow":4,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}}
{"IsHide":true,"SheetId":5,"Name":"Commercial Carbon Calculator","HiddenRow":5,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}}